## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-10-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.04 | 0.051 |  |  |  | 0.055 | 0.055
2 | 0.052 |  |  | 0.058 | 0.053 |  | 0.058
3 |  |  | 0.043 | 0.048 |  |  | 0.048
4 | 0.051 | 0.049 |  | 0.048 |  |  | 0.051
5 |  |  | 0.062 | 0.048 |  |  | 0.062
6 |  | 0.049 | 0.048 |  | 0.054 |  | 0.054
7 |  |  | 0.049 | 0.036 |  |  | 0.049
8 | 0.067 | 0.061 |  |  | 0.058 |  | 0.067
9 |  | 0.072 | 0.065 |  |  | 0.066 | 0.072
10 |  | 0.053 |  | 0.063 |  |  | 0.063
11 |  |  | 0.065 |  |  | 0.066 | 0.066
12 |  | 0.065 | 0.059 |  |  |  | 0.065
13 |  | 0.055 | 0.067 |  | 0.051 |  | 0.067
14 | 0.054 |  |  | 0.069 | 0.055 |  | 0.069
15 |  |  | 0.058 | 0.056 |  |  | 0.058
16 |  | 0.049 | 0.059 |  | 0.05 |  | 0.059
17 |  |  |  | 0.07 | 0.064 |  | 0.07
18 |  | 0.054 | 0.059 |  |  | 0.049 | 0.059
19 |  | 0.061 |  | 0.062 |  |  | 0.062
20 |  |  | 0.076 | 0.062 |  |  | 0.076
21 | 0.056 | 0.049 |  |  | 0.058 |  | 0.058
22 |  |  | 0.078 | 0.065 |  |  | 0.078
23 |  | 0.063 | 0.052 |  |  | 0.051 | 0.063
24 |  |  | 0.072 | 0.064 |  |  | 0.072
25 |  | 0.052 | 0.052 |  |  |  | 0.052
26 | 0.063 | 0.067 |  | 0.059 |  |  | 0.067
27 |  |  | 0.074 | 0.077 |  |  | 0.077
28 |  | 0.068 | 0.069 |  |  |  | 0.068
29 |  |  | 0.079 | 0.083 |  |  | 0.083
30 | 0.066 | 0.068 |  |  |  | 0.059 | 0.068
31 |  |  | 0.059 | 0.063 |  |  | 0.063
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 11-7-25
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226-D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2025-10-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.03 | 58 | 59.74 | 14.6 | 6.9 | 27.0483 | YES | 20
2 | 0.99 | 58 | 57.42 | 14.8 | 6.93 | 26.8647 | YES | 20
3 | 0.96 | 58 | 55.68 | 14.5 | 6.78 | 25.8331 | YES | 20
4 | 0.98 | 58 | 56.84 | 14.8 | 6.99 | 27.4394 | YES | 20
5 | 1.01 | 58 | 58.58 | 14.3 | 6.94 | 27.9463 | YES | 20
6 | 1.03 | 58 | 59.74 | 14.8 | 7.02 | 27.906 | YES | 20
7 | 0.97 | 58 | 56.26 | 14.9 | 6.95 | 26.8232 | YES | 20
8 | 0.97 | 58 | 56.26 | 14 | 6.91 | 28.0682 | YES | 20
9 | 1.05 | 58 | 60.9 | 14.3 | 6.81 | 26.7498 | YES | 20
10 | 1.03 | 58 | 59.74 | 14.5 | 6.98 | 28.0517 | YES | 20
11 | 0.99 | 58 | 57.42 | 14.7 | 6.79 | 25.6721 | YES | 20
12 | 0.96 | 58 | 55.68 | 14.8 | 6.86 | 26.0842 | YES | 20
13 | 1.01 | 58 | 58.58 | 14.6 | 7.01 | 28.1127 | YES | 20
14 | 1.04 | 58 | 60.32 | 15.3 | 6.89 | 25.7424 | YES | 20
15 | 1.03 | 58 | 59.74 | 15.5 | 6.87 | 25.1819 | YES | 20
16 | 0.97 | 58 | 56.26 | 14.9 | 6.92 | 26.5255 | YES | 20
17 | 1.06 | 58 | 61.48 | 15.2 | 6.85 | 25.5909 | YES | 20
18 | 1.04 | 58 | 60.32 | 15.6 | 6.88 | 25.1356 | YES | 20
19 | 1 | 58 | 58 | 15.2 | 6.99 | 26.7754 | YES | 20
20 | 0.97 | 58 | 56.26 | 14.8 | 6.82 | 25.728 | YES | 20
21 | 1.02 | 58 | 59.16 | 14.9 | 7.06 | 28.1029 | YES | 20
22 | 1.03 | 58 | 59.74 | 14.4 | 6.85 | 26.9079 | YES | 20
23 | 1 | 58 | 58 | 15.1 | 6.92 | 26.2624 | YES | 20
24 | 0.97 | 58 | 56.26 | 14.2 | 7.02 | 28.8501 | YES | 20
25 | 0.98 | 58 | 56.84 | 14.6 | 6.91 | 26.9943 | YES | 20
26 | 0.96 | 58 | 55.68 | 14.9 | 6.87 | 26.0066 | YES | 20
27 | 0.97 | 58 | 56.26 | 15.4 | 6.89 | 25.3661 | YES | 20
28 | 1.03 | 58 | 59.74 | 14.9 | 6.81 | 25.6366 | YES | 20
29 | 1.06 | 58 | 61.48 | 14.3 | 6.95 | 28.211 | YES | 20
30 | 1.04 | 58 | 60.32 | 14.8 | 6.88 | 26.5208 | YES | 20
31 | 1 | 58 | 58 | 14.1 | 6.78 | 26.6568 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2