## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-12-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.073 | 0.059 |  |  | 0.061 | 0.055 | 0.073
2 |  |  | 0.045 | 0.053 | 0.051 |  | 0.053
3 |  | 0.049 | 0.044 |  |  |  | 0.049
4 | 0.039 | 0.036 |  | 0.062 | 0.054 |  | 0.062
5 |  |  | 0.072 | 0.068 |  |  | 0.072
6 | 0.068 | 0.066 |  |  |  | 0.049 | 0.068
7 |  |  | 0.056 | 0.057 |  |  | 0.057
8 |  | 0.044 | 0.046 |  | 0.056 |  | 0.056
9 |  | 0.058 | 0.05 |  |  | 0.044 | 0.058
10 |  |  | 0.071 | 0.065 |  |  | 0.071
11 |  |  | 0.063 | 0.068 |  |  | 0.068
12 | 0.053 | 0.051 |  |  | 0.062 |  | 0.062
13 |  | 0.063 | 0.05 |  |  |  | 0.063
14 | 0.059 | 0.049 |  |  | 0.062 |  | 0.062
15 |  |  | 0.073 | 0.076 |  |  | 0.076
16 | 0.056 | 0.058 |  |  | 0.049 |  | 0.058
17 |  |  | 0.053 | 0.059 |  |  | 0.059
18 |  | 0.054 | 0.055 |  |  | 0.049 | 0.055
19 |  |  |  | 0.059 | 0.055 |  | 0.059
20 | 0.052 | 0.056 |  |  | 0.052 |  | 0.056
21 |  |  | 0.056 | 0.049 |  |  | 0.056
22 |  | 0.063 | 0.057 |  |  | 0.059 | 0.063
23 |  | 0.055 | 0.043 |  |  |  | 0.055
24 |  |  |  | 0.059 | 0.051 |  | 0.059
25 | 0.041 | 0.038 |  |  | 0.051 |  | 0.051
26 |  | 0.066 | 0.079 |  |  |  | 0.079
27 |  |  |  | 0.081 | 0.073 |  | 0.081
28 | 0.06 | 0.063 |  | 0.059 |  |  | 0.063
29 |  |  | 0.051 | 0.056 |  |  | 0.056
30 | 0.044 |  |  |  | 0.067 | 0.059 | 0.067
31 |  | 0.055 | 0.054 |  |  |  | 0.055
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 01-09-26
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226-D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2025-12-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.98 | 58 | 56.84 | 13.4 | 6.99 | 30.1313 | YES | 20
2 | 0.83 | 58 | 48.14 | 13.5 | 6.87 | 28.1411 | YES | 20
3 | 1.02 | 58 | 59.16 | 13.9 | 6.77 | 26.9776 | YES | 20
4 | 0.95 | 58 | 55.1 | 12.8 | 6.98 | 31.1395 | YES | 20
5 | 1.04 | 58 | 60.32 | 12.7 | 6.85 | 30.1815 | YES | 20
6 | 0.95 | 58 | 55.1 | 13.5 | 7.03 | 30.2743 | YES | 20
7 | 0.88 | 58 | 51.04 | 13.4 | 6.9 | 28.8113 | YES | 20
8 | 0.92 | 58 | 53.36 | 13 | 6.82 | 28.8575 | YES | 20
9 | 1.05 | 58 | 60.9 | 12.8 | 6.8 | 29.4633 | YES | 20
10 | 0.98 | 58 | 56.84 | 13.3 | 6.85 | 28.7979 | YES | 20
11 | 1.01 | 58 | 58.58 | 13.6 | 6.79 | 27.6986 | YES | 20
12 | 0.96 | 58 | 55.68 | 13.3 | 6.95 | 29.8185 | YES | 20
13 | 0.99 | 58 | 57.42 | 13.3 | 6.91 | 29.48 | YES | 20
14 | 0.96 | 58 | 55.68 | 12.4 | 6.81 | 30.8832 | YES | 20
15 | 0.99 | 58 | 57.42 | 12.9 | 6.86 | 29.7218 | YES | 20
16 | 0.98 | 58 | 56.84 | 13.8 | 6.9 | 28.3731 | YES | 20
17 | 0.91 | 58 | 52.78 | 14.1 | 6.94 | 28.001 | YES | 20
18 | 0.96 | 58 | 55.68 | 13.7 | 6.85 | 27.9739 | YES | 20
19 | 1.02 | 58 | 59.16 | 13.5 | 6.77 | 27.7097 | YES | 20
20 | 1.05 | 58 | 60.9 | 12.4 | 6.75 | 30.563 | YES | 20
21 | 1 | 58 | 58 | 12.8 | 6.79 | 29.1872 | YES | 20
22 | 0.96 | 58 | 55.68 | 13.1 | 6.88 | 29.4449 | YES | 20
23 | 1.05 | 58 | 60.9 | 12.7 | 6.73 | 28.9003 | YES | 20
24 | 1.02 | 58 | 59.16 | 12.6 | 6.79 | 29.6474 | YES | 20
25 | 0.94 | 58 | 54.52 | 12.4 | 6.81 | 30.8166 | YES | 20
26 | 0.96 | 58 | 55.68 | 12.7 | 6.73 | 28.6049 | YES | 20
27 | 0.99 | 58 | 57.42 | 13 | 6.78 | 28.6603 | YES | 20
28 | 0.98 | 58 | 56.84 | 13.3 | 6.7 | 27.237 | YES | 20
29 | 1.04 | 58 | 60.32 | 12.7 | 6.67 | 28.2313 | YES | 20
30 | 0.89 | 58 | 51.62 | 12.3 | 6.71 | 29.8294 | YES | 20
31 | 0.98 | 58 | 56.84 | 12.5 | 6.79 | 29.7102 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2