## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2026-01-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.055 | 0.059 |  |  | 0.066 |  | 0.066
2 |  | 0.062 | 0.056 |  | 0.049 |  | 0.062
3 |  | 0.054 | 0.043 |  |  |  | 0.054
4 |  |  |  | 0.039 | 0.039 |  | 0.039
5 |  |  | 0.044 | 0.044 |  |  | 0.044
6 | 0.039 | 0.036 |  |  | 0.033 |  | 0.039
7 |  |  | 0.046 | 0.051 |  |  | 0.051
8 | 0.041 | 0.043 |  |  | 0.031 |  | 0.043
9 |  |  |  | 0.059 | 0.046 |  | 0.059
10 |  | 0.052 | 0.051 |  |  | 0.044 | 0.052
11 |  |  | 0.036 | 0.059 |  |  | 0.059
12 | 0.041 | 0.039 |  |  |  |  | 0.041
13 |  | 0.052 |  | 0.041 | 0.053 |  | 0.053
14 |  |  | 0.039 | 0.049 |  |  | 0.049
15 |  | 0.036 | 0.038 |  |  | 0.045 | 0.045
16 |  |  | 0.045 | 0.053 |  |  | 0.053
17 |  |  | 0.035 | 0.036 |  |  | 0.036
18 | 0.033 | 0.046 |  |  | 0.035 |  | 0.046
19 |  | 0.069 | 0.06 | 0.055 |  |  | 0.069
20 | 0.041 |  |  | 0.052 | 0.06 |  | 0.06
21 |  |  | 0.058 | 0.048 |  |  | 0.058
22 |  | 0.048 | 0.051 |  |  | 0.033 | 0.051
23 |  |  | 0.067 | 0.066 |  |  | 0.067
24 |  | 0.059 | 0.055 |  |  |  | 0.059
25 | 0.035 |  |  | 0.036 | 0.047 |  | 0.047
26 |  |  | 0.053 | 0.044 |  |  | 0.053
27 |  | 0.052 |  | 0.036 | 0.048 |  | 0.052
28 |  | 0.029 | 0.033 |  |  | 0.051 | 0.051
29 |  |  | 0.049 | 0.055 |  |  | 0.055
30 |  | 0.055 | 0.051 |  | 0.049 |  | 0.055
31 | 0.036 |  |  | 0.055 | 0.059 |  | 0.059
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 02-09-26
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226-D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2026-01-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.06 | 58 | 61.48 | 12.9 | 6.76 | 28.8688 | YES | 20
2 | 0.99 | 58 | 57.42 | 12.5 | 6.81 | 29.9656 | YES | 20
3 | 1.02 | 58 | 59.16 | 13.1 | 6.77 | 28.4611 | YES | 20
4 | 1.01 | 58 | 58.58 | 12.9 | 6.75 | 28.5981 | YES | 20
5 | 1.01 | 58 | 58.58 | 12.4 | 6.67 | 29.6291 | YES | 20
6 | 0.96 | 58 | 55.68 | 12.4 | 6.71 | 29.8666 | YES | 20
7 | 1.04 | 58 | 60.32 | 12.1 | 6.77 | 31.3221 | YES | 20
8 | 1.05 | 58 | 60.9 | 12.6 | 6.62 | 27.9296 | YES | 20
9 | 1.02 | 58 | 59.16 | 12.1 | 6.68 | 30.325 | YES | 20
10 | 1 | 58 | 58 | 12.6 | 6.77 | 29.3612 | YES | 20
11 | 1.06 | 58 | 61.48 | 12.3 | 6.89 | 32.2751 | YES | 20
12 | 1.02 | 58 | 59.16 | 12.4 | 6.64 | 29.3659 | YES | 20
13 | 1 | 58 | 58 | 12.5 | 6.68 | 28.587 | YES | 20
14 | 0.95 | 58 | 55.1 | 12.8 | 6.67 | 27.7562 | YES | 20
15 | 0.98 | 58 | 56.84 | 12.7 | 6.69 | 28.2476 | YES | 20
16 | 1.01 | 58 | 58.58 | 12.5 | 6.71 | 28.9401 | YES | 20
17 | 1.05 | 58 | 60.9 | 12.1 | 6.88 | 32.5415 | YES | 20
18 | 1.04 | 58 | 60.32 | 12.2 | 6.76 | 31.0207 | YES | 20
19 | 1 | 58 | 58 | 12 | 6.74 | 31.0695 | YES | 20
20 | 0.99 | 58 | 57.42 | 12.4 | 6.78 | 30.673 | YES | 20
21 | 0.98 | 58 | 56.84 | 12.5 | 6.81 | 29.9314 | YES | 20
22 | 0.96 | 58 | 55.68 | 12.5 | 6.67 | 28.3512 | YES | 20
23 | 1.02 | 58 | 59.16 | 12.1 | 6.65 | 30.0223 | YES | 20
24 | 1.06 | 58 | 61.48 | 11.5 | 6.69 | 31.7364 | YES | 20
25 | 1.03 | 58 | 59.74 | 11.6 | 6.54 | 29.8927 | YES | 20
26 | 1.01 | 58 | 58.58 | 12.1 | 6.68 | 30.2924 | YES | 20
27 | 0.98 | 58 | 56.84 | 12 | 6.77 | 31.3167 | YES | 20
28 | 0.97 | 58 | 56.26 | 11.8 | 6.64 | 30.3274 | YES | 20
29 | 0.95 | 58 | 55.1 | 11.6 | 6.69 | 31.1636 | YES | 20
30 | 0.99 | 58 | 57.42 | 12.1 | 6.82 | 31.682 | YES | 20
31 | 1.01 | 58 | 58.58 | 11.5 | 6.83 | 33.0945 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2