## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Jackson
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-09-01
System Name: | Anglers Cove SCHWC |  |  | ID#: 41 | 01483 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
2 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
3 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
4 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
5 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
6 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
7 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
8 | 0.06 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.06
9 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
10 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
11 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
12 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
13 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
14 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
15 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
16 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
17 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
18 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
19 | 0.035 | 0.04 | 0.04 | 0.035 | 0.035 | 0.035 | 0.04
20 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
21 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
22 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
23 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
24 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
25 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
26 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
27 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
28 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
29 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
30 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
31 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Dan Perkins
[5 empty] | SIGNATURE: |  |  | 2024-10-01
[5 empty] | PHONE #: (541) 941-3951 |  |  | CERT #: 2339
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Anglers Cove SCHWC |  | ID#: 41 | 01483 | Month/Year: | 2024-09-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1800 | 1.2 | 90 | 108 | 17.4 | 7.3 | 26.5312 | YES | 20
1800 | 1.2 | 90 | 108 | 17.5 | 7.32 | 26.5509 | YES | 20
1500 | 1.2 | 90 | 108 | 17.4 | 7.33 | 26.829 | YES | 20
2045 | 1.2 | 90 | 108 | 17.1 | 7.36 | 27.6803 | YES | 20
1915 | 1.2 | 90 | 108 | 1.4 | 7.38 | 80.7413 | YES | 20
1715 | 1.2 | 90 | 108 | 17.5 | 7.39 | 27.2513 | YES | 20
2145 | 1.2 | 90 | 108 | 16.8 | 7.34 | 28.0324 | YES | 20
1315 | 1.2 | 90 | 108 | 17 | 7.3 | 27.2516 | YES | 20
1745 | 1.2 | 90 | 108 | 17.1 | 7.32 | 27.2718 | YES | 20
1715 | 1.2 | 90 | 108 | 17 | 7.31 | 27.3531 | YES | 20
1915 | 1.2 | 90 | 108 | 16.1 | 7.24 | 28.3049 | YES | 20
1815 | 1.2 | 90 | 108 | 15.8 | 7.25 | 28.9857 | YES | 20
2000 | 1.2 | 90 | 108 | 15.6 | 7.26 | 29.4848 | YES | 20
1230 | 1.2 | 90 | 108 | 15.1 | 7.24 | 30.2606 | YES | 20
1930 | 1.2 | 90 | 108 | 15.2 | 7.21 | 29.7267 | YES | 20
1800 | 1.2 | 90 | 108 | 15.1 | 7.26 | 30.4858 | YES | 20
1730 | 1.2 | 90 | 108 | 15 | 7.24 | 30.4633 | YES | 20
1800 | 1.2 | 90 | 108 | 15.1 | 7.22 | 30.037 | YES | 20
1845 | 1.2 | 90 | 108 | 15.1 | 7.25 | 30.373 | YES | 20
900 | 1.2 | 90 | 108 | 14.8 | 7.21 | 30.5312 | YES | 20
900 | 1.2 | 90 | 108 | 14.7 | 7.19 | 30.5087 | YES | 20
1500 | 1.2 | 90 | 108 | 15.1 | 7.21 | 29.9259 | YES | 20
1630 | 1.2 | 90 | 108 | 15.3 | 7.29 | 30.4179 | YES | 20
1700 | 1.2 | 90 | 108 | 15.4 | 7.33 | 30.6669 | YES | 20
1700 | 1.2 | 90 | 108 | 15.1 | 7.3 | 30.9411 | YES | 20
1700 | 1.2 | 90 | 108 | 15.3 | 7.31 | 30.6443 | YES | 20
1600 | 1.2 | 90 | 108 | 15.4 | 7.33 | 30.6669 | YES | 20
1200 | 1.2 | 90 | 108 | 15.1 | 7.23 | 30.1486 | YES | 20
1645 | 1.2 | 90 | 108 | 15 | 7.25 | 30.5764 | YES | 20
1800 | 1.2 | 90 | 108 | 14.9 | 7.31 | 31.473 | YES | 20
N/A | N/A | N/A | #VALUE! | N/A | N/A | #VALUE! | #VALUE! | N/A
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2