## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Jackson
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-10-01
System Name: | Anglers Cove SCHWC |  |  | ID#: 41 | 01483 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
2 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
3 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
4 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
5 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
6 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
7 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
8 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
9 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
10 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
11 | 0.035 | 0.035 | 0.035 | 0.055 | 0.06 | 0.035 | 0.06
12 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
13 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
14 | 0.035 | 0.035 | 0.06 | 0.07 | 0.07 | 0.035 | 0.07
15 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
16 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
17 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
18 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
19 | 0.035 | 0.04 | 0.04 | 0.035 | 0.035 | 0.035 | 0.04
20 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
21 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
22 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
23 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
24 | 0.035 | 0.035 | 0.035 | 0.035 | 0.04 | 0.035 | 0.04
25 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
26 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.05 | 0.05
27 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
28 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
29 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
30 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
31 | 0.035 | 0.035 | 0.035 | 0.05 | 0.07 | 0.035 | 0.07
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Dan Perkins
[5 empty] | SIGNATURE: |  |  | 2024-11-04
[5 empty] | PHONE #: (541) 941-3951 |  |  | CERT #: 2339
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Anglers Cove SCHWC |  | ID#: 41 | 01483 | Month/Year: | 2024-10-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1800 | 1.2 | 90 | 108 | 15.1 | 7.31 | 31.0559 | YES | 20
1645 | 1.2 | 90 | 108 | 14.8 | 7.3 | 31.5664 | YES | 20
1600 | 1.2 | 90 | 108 | 14.6 | 7.29 | 31.8719 | YES | 20
1200 | 1.2 | 90 | 108 | 14.4 | 7.23 | 31.5901 | YES | 20
1345 | 1.2 | 90 | 108 | 14.2 | 7.25 | 32.252 | YES | 20
1630 | 1.2 | 90 | 108 | 14.1 | 7.26 | 32.588 | YES | 20
1730 | 1.2 | 90 | 108 | 11.3 | 7.33 | 40.6605 | YES | 20
1700 | 1.2 | 90 | 108 | 11.1 | 7.31 | 40.9097 | YES | 20
1800 | 1.2 | 90 | 108 | 11.2 | 7.26 | 39.9418 | YES | 20
1715 | 1.2 | 90 | 108 | 11 | 7.28 | 40.7498 | YES | 20
2245 | 1.2 | 90 | 108 | 11.1 | 7.24 | 39.9246 | YES | 20
1715 | 1.2 | 90 | 108 | 11.3 | 7.26 | 39.6821 | YES | 20
1030 | 1.2 | 90 | 108 | 11.2 | 7.21 | 39.254 | YES | 20
1615 | 1.2 | 90 | 108 | 11 | 7.29 | 40.8921 | YES | 20
1815 | 1.2 | 90 | 108 | 10.9 | 7.23 | 40.3089 | YES | 20
1645 | 1.2 | 90 | 108 | 10.8 | 7.2 | 40.1516 | YES | 20
1830 | 1.2 | 90 | 108 | 10.8 | 7.18 | 39.8733 | YES | 20
1700 | 1.2 | 90 | 108 | 10.6 | 7.2 | 40.6798 | YES | 20
1130 | 1.2 | 90 | 108 | 10.4 | 7.17 | 40.7867 | YES | 20
1530 | 1.2 | 90 | 108 | 10.8 | 7.19 | 40.0122 | YES | 20
1800 | 1.2 | 90 | 108 | 10.8 | 7.21 | 40.2916 | YES | 20
1715 | 1.2 | 90 | 108 | 10.7 | 7.2 | 40.4147 | YES | 20
1800 | 1.2 | 90 | 108 | 9.8 | 7.18 | 42.5719 | YES | 20
1815 | 1.2 | 90 | 108 | 9.7 | 7.17 | 42.7029 | YES | 20
1800 | 1.2 | 90 | 108 | 9.6 | 7.17 | 42.9847 | YES | 20
200 | 1.2 | 90 | 108 | 9.5 | 7.21 | 43.8807 | YES | 20
1745 | 1.2 | 90 | 108 | 9.3 | 7.17 | 43.8426 | YES | 20
1900 | 1.2 | 90 | 108 | 9 | 7.16 | 44.5624 | YES | 20
1830 | 1.2 | 90 | 108 | 8.7 | 7.18 | 45.7771 | YES | 20
1900 | 1.2 | 90 | 108 | 8.7 | 7.14 | 45.1358 | YES | 20
1715 | 1.2 | 90 | 108 | 8.6 | 7.16 | 45.7572 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2