## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Jackson
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-11-01
System Name: | Anglers Cove SCHWC |  |  | ID#: 41 | 01483 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
2 | 0.035 | 0.045 | 0.06 | 0.05 | 0.05 | 0.05 | 0.06
3 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.05 | 0.08
4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
6 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.06 | 0.06
7 | 0.06 | 0.06 | 0.06 | 0.08 | 0.05 | 0.05 | 0.08
8 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
9 | 0.075 | 0.045 | 0.075 | 0.075 | 0.05 | 0.035 | 0.075
10 | 0.035 | 0.035 | 0.06 | 0.035 | 0.035 | 0.035 | 0.06
11 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
12 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.05
13 | 0.05 | 0.05 | 0.05 | 0.045 | 0.045 | OFF | 0.05
14 | 0.28 | 0.1 | 0.28 | OFF | OFF | OFF | 0.28
15 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
16 | OFF | OFF | OFF | OFF | OFF | 0.07 | 0.07
17 | 0.035 | 0.035 | 0.12 | 0.035 | 0.035 | 0.05 | 0.12
18 | 0.16 | 0.28 | OFF | OFF | OFF | OFF | 0.28
19 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
20 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
21 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
22 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
23 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
24 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
25 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
26 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
27 | OFF | OFF | OFF | OFF | 0.1 | 0.06 | 0.1
28 | 0.035 | 0.07 | 0.035 | 0.08 | 0.035 | 0.07 | 0.08
29 | 0.07 | 0.035 | 0.08 | 0.08 | 0.035 | 0.035 | 0.08
30 | 0.035 | 0.035 | 0.035 | 0.07 | 0.05 | 0.035 | 0.07
31 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Dan Perkins
[5 empty] | SIGNATURE: |  |  | 2024-12-02
[5 empty] | PHONE #: (541) 941-3951 |  |  | CERT #: 2339
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Anglers Cove SCHWC |  | ID#: 41 | 01483 | Month/Year: | 2024-11-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1815 | 1.2 | 180 | 216 | 8.5 | 7.15 | 45.899 | YES | 10
1115 | 1.2 | 180 | 216 | 8.4 | 7.14 | 46.0413 | YES | 10
1715 | 1.2 | 180 | 216 | 8.3 | 7.16 | 46.6765 | YES | 10
1730 | 1.2 | 180 | 216 | 8.1 | 7.15 | 47.1334 | YES | 10
1730 | 1.2 | 180 | 216 | 8 | 7.16 | 47.6161 | YES | 10
1800 | 1.2 | 180 | 216 | 7.9 | 7.14 | 47.5953 | YES | 10
1700 | 1.2 | 180 | 216 | 7.8 | 7.14 | 47.913 | YES | 10
1830 | 1.2 | 180 | 216 | 7.8 | 7.16 | 48.2541 | YES | 10
1430 | 1.2 | 180 | 216 | 7.8 | 7.15 | 48.0832 | YES | 10
1145 | 1.2 | 180 | 216 | 7.7 | 7.14 | 48.233 | YES | 10
1430 | 1.2 | 180 | 216 | 7.6 | 7.17 | 49.0755 | YES | 10
1745 | 1.2 | 180 | 216 | 7.6 | 7.17 | 49.0755 | YES | 10
1730 | 1.2 | 180 | 216 | 7.5 | 7.13 | 48.7067 | YES | 10
1730 | 1.2 | 180 | 216 | 7.4 | 7.21 | 50.4484 | YES | 10
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
1230 | 1.2 | 180 | 216 | 7.5 | 7.18 | 49.5801 | YES | 10
1400 | 1.2 | 180 | 216 | 7.4 | 7.16 | 49.5583 | YES | 10
1900 | 1.2 | 180 | 216 | 7.3 | 7.17 | 50.0683 | YES | 10
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
1800 | 1.2 | 90 | 108 | 7 | 7.18 | 51.2656 | YES | 10
1130 | 1.2 | 90 | 108 | 6.9 | 7.16 | 51.2431 | YES | 10
1400 | 1.2 | 90 | 108 | 6.8 | 7.16 | 51.5875 | YES | 10
1615 | 1.2 | 90 | 108 | 6.7 | 7.15 | 51.7492 | YES | 10
N/A | N/A | N/A | #VALUE! | N/A | N/A | #VALUE! | #VALUE! | N/A
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2