## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Jackson
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-03-01
System Name: | Anglers Cove SCHWC |  |  | ID#: 41 | 01483 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.17 | 0.09 | 0.09 | 0.17
2 | 0.11 | 0.11 | 0.08 | 0.28 | 0.08 | 0.07 | 0.28
3 | 0.07 | 0.035 | 0.045 | 0.055 | 0.1 | 0.1 | 0.1
4 | 0.05 | 0.05 | 0.045 | 0.05 | 0.07 | 0.09 | 0.09
5 | 0.09 | 0.05 | 0.04 | 0.035 | 0.04 | 0.045 | 0.09
6 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | OFF | 0.045
7 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
8 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
9 | OFF | OFF | OFF | OFF | 0.05 | 0.035 | 0.05
10 | 0.065 | 0.035 | 0.12 | 0.12 | 0.17 | 0.035 | 0.17
11 | 0.035 | 0.035 | 0.04 | 0.105 | 0.105 | 0.05 | 0.105
12 | 0.035 | 0.035 | 0.035 | 0.105 | 0.06 | 0.145 | 0.145
13 | 0.035 | 0.035 | 0.035 | 0.035 | 0.085 | 0.035 | 0.085
14 | 0.035 | 0.035 | 0.045 | 0.12 | 0.12 | 0.07 | 0.12
15 | 0.035 | 0.035 | 0.06 | 0.16 | 0.28 | 0.05 | 0.28
16 | 0.05 | 0.035 | 0.035 | OFF | OFF | OFF | 0.05
17 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
18 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
19 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
20 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
21 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
22 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
23 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
24 | OFF | OFF | OFF | OFF | OFF | 0.05 | 0.05
25 | 0.035 | 0.035 | 0.115 | 0.15 | 0.15 | 0.11 | 0.15
26 | 0.07 | 0.07 | 0.055 | 0.235 | 0.17 | 0.05 | 0.235
27 | 0.05 | 0.035 | 0.09 | 0.11 | 0.11 | 0.035 | 0.11
28 | 0.045 | 0.035 | 0.035 | 0.075 | 0.225 | 0.09 | 0.225
29 | 0.075 | 0.075 | 0.085 | 0.095 | 0.2 | 0.14 | 0.2
30 | 0.035 | 0.035 | 0.035 | 0.035 | 0.06 | 0.035 | 0.06
31 | 0.035 | 0.035 | 0.035 | 0.11 | 0.035 | 0.035 | 0.11
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Dan Perkins
[5 empty] | SIGNATURE: |  |  | 2025-04-02
[5 empty] | PHONE #: (541) 941-3951 |  |  | CERT #: 2339
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Anglers Cove SCHWC |  | ID#: 41 | 01483 | Month/Year: | 2025-03-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1530 | 1.2 | 180 | 216 | 6.4 | 7.16 | 52.9904 | YES | 10
1620 | 1.2 | 180 | 216 | 6.5 | 7.18 | 53.0138 | YES | 10
1715 | 1.2 | 180 | 216 | 6.7 | 7.16 | 51.9344 | YES | 10
1800 | 1.2 | 180 | 216 | 6.8 | 7.17 | 51.772 | YES | 10
1715 | 1.2 | 180 | 216 | 6.8 | 7.18 | 51.9573 | YES | 10
1800 | 1.2 | 180 | 216 | 6.8 | 7.17 | 51.772 | YES | 10
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
1500 | 1.2 | 180 | 216 | 6.8 | 7.16 | 51.5875 | YES | 10
1715 | 1.2 | 180 | 216 | 6.9 | 7.18 | 51.6102 | YES | 10
1800 | 1.2 | 180 | 216 | 6.7 | 7.16 | 51.9344 | YES | 10
1730 | 1.2 | 180 | 216 | 6.9 | 7.19 | 51.7948 | YES | 10
1730 | 1.2 | 180 | 216 | 8.1 | 7.17 | 47.4685 | YES | 10
1700 | 1.2 | 180 | 216 | 8.3 | 7.21 | 47.51 | YES | 10
1800 | 1.2 | 180 | 216 | 8.1 | 7.19 | 47.8061 | YES | 10
1815 | 1.2 | 180 | 216 | 8.1 | 7.2 | 47.9759 | YES | 10
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
1800 | 1.2 | 180 | 216 | 8.3 | 7.16 | 46.6765 | YES | 10
1815 | 1.2 | 180 | 216 | 8.4 | 7.17 | 46.532 | YES | 10
1800 | 1.2 | 180 | 216 | 8.6 | 7.19 | 46.2446 | YES | 10
1800 | 1.2 | 180 | 216 | 8.6 | 7.18 | 46.0815 | YES | 10
1730 | 1.2 | 180 | 216 | 8.5 | 7.16 | 46.0614 | YES | 10
2100 | 1.2 | 180 | 216 | 8.7 | 7.21 | 46.2647 | YES | 10
1430 | 1.2 | 180 | 216 | 8.8 | 7.2 | 45.7971 | YES | 10
1800 | 1.2 | 180 | 216 | 8.7 | 7.17 | 45.6158 | YES | 10
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2