## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Jackson
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-04-01
System Name: | Anglers Cove SCHWC |  |  | ID#: 41 | 01483 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.035 | 0.035 | 0.06 | 0.11 | 0.08 | 0.035 | 0.11
2 | 0.035 | 0.035 | 0.035 | 0.105 | 0.05 | 0.035 | 0.105
3 | 0.035 | 0.035 | 0.11 | 0.085 | 0.17 | 0.17 | 0.17
4 | OFF | 0.04 | 0.04 | 0.04 | 0.035 | 0.035 | 0.04
5 | OFF | 0.065 | 0.135 | 0.22 | 0.28 | 0.035 | 0.28
6 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
7 | 0.035 | 0.035 | 0.035 | 0.035 | 0.12 | 0.035 | 0.12
8 | 0.035 | 0.035 | 0.1 | 0.06 | 0.06 | 0.035 | 0.1
9 | 0.035 | 0.035 | 0.05 | 0.035 | 0.035 | 0.035 | 0.05
10 | 0.035 | 0.035 | 0.035 | 0.09 | 0.11 | OFF | 0.11
11 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
12 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
13 | OFF | OFF | OFF | 0.07 | 0.035 | 0.035 | 0.07
14 | 0.035 | 0.035 | 0.035 | 0.07 | 0.11 | 0.035 | 0.11
15 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
16 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
17 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
18 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.135 | 0.135
19 | OFF | OFF | 0.21 | 0.265 | 0.035 | 0.035 | 0.265
20 | 0.035 | 0.035 | 0.035 | 0.035 | 0.065 | 0.035 | 0.065
21 | 0.035 | 0.035 | 0.04 | 0.04 | 0.04 | 0.035 | 0.04
22 | 0.035 | 0.035 | 0.035 | 0.05 | 0.035 | 0.035 | 0.05
23 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
24 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
25 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
26 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
27 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
28 | OFF | OFF | OFF | OFF | OFF | 0.035 | 0.035
29 | 0.035 | 0.035 | 0.08 | 0.075 | 0.11 | 0.035 | 0.11
30 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
31 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Dan Perkins
[5 empty] | SIGNATURE: |  |  | 2025-05-06
[5 empty] | PHONE #: (541) 941-3951 |  |  | CERT #: 2339
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Anglers Cove SCHWC |  | ID#: 41 | 01483 | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1800 | 1.2 | 180 | 216 | 8.6 | 7.16 | 45.7572 | YES | 10
1715 | 1.2 | 180 | 216 | 8.7 | 7.18 | 45.7771 | YES | 10
1900 | 1.2 | 180 | 216 | 8.6 | 7.18 | 46.0815 | YES | 10
1715 | 1.2 | 180 | 216 | 8.7 | 7.19 | 45.939 | YES | 10
1930 | 1.2 | 180 | 216 | 8.8 | 7.2 | 45.7971 | YES | 10
1600 | 1.2 | 180 | 216 | 8.8 | 7.18 | 45.475 | YES | 10
1800 | 1.2 | 180 | 216 | 8.8 | 7.17 | 45.3149 | YES | 10
1900 | 1.2 | 180 | 216 | 8.9 | 7.18 | 45.1751 | YES | 10
1715 | 1.2 | 180 | 216 | 9 | 7.19 | 45.0357 | YES | 10
1900 | 1.2 | 180 | 216 | 9 | 7.18 | 44.8773 | YES | 10
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
1300 | 1.2 | 180 | 216 | 8.9 | 7.16 | 44.8578 | YES | 10
1900 | 1.2 | 180 | 216 | 9.1 | 7.19 | 44.739 | YES | 10
1700 | 1.2 | 180 | 216 | 12 | 7.6 | 42.6787 | YES | 10
1815 | 1.2 | 180 | 216 | 12.3 | 7.61 | 41.9925 | YES | 10
1730 | 1.2 | 90 | 108 | 12.4 | 7.63 | 42.0107 | YES | 20
2000 | 1.2 | 90 | 108 | 12.5 | 7.52 | 39.8966 | YES | 20
1445 | 1.2 | 90 | 108 | 12.3 | 7.49 | 40.2707 | YES | 20
1730 | 1.2 | 90 | 108 | 12.4 | 7.52 | 40.4285 | YES | 20
1730 | 1.2 | 90 | 108 | 12.3 | 7.49 | 40.2707 | YES | 20
1730 | 1.2 | 90 | 108 | 12.2 | 7.57 | 41.682 | YES | 20
1730 | 1.2 | 90 | 108 | 12.1 | 7.56 | 41.8099 | YES | 20
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
OFF | OFF | OFF | #VALUE! | OFF | OFF | #VALUE! | #VALUE! | OFF
1500 | 1.2 | 90 | 108 | 12.1 | 7.53 | 41.374 | YES | 20
1900 | 1.2 | 90 | 108 | 12 | 7.51 | 41.3561 | YES | 20
1900 | 1.2 | 90 | 108 | 12.2 | 7.53 | 41.1039 | YES | 20
N/A | N/A | N/A | #VALUE! | N/A | N/A | #VALUE! | #VALUE! | N/A
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2