## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Jackson
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-05-01
System Name: | Anglers Cove SCHWC |  |  | ID#: 41 | 01483 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.035 | 0.15
2 | 0.035 | 0.035 | 0.04 | 0.065 | 0.1 | 0.035 | 0.1
3 | 0.035 | 0.035 | 0.05 | 0.085 | 0.035 | 0.035 | 0.085
4 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
5 | 0.035 | 0.035 | 0.035 | 0.035 | 0.04 | 0.035 | 0.04
6 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
7 | 0.035 | 0.035 | 0.035 | 0.055 | 0.075 | 0.035 | 0.075
8 | 0.035 | 0.035 | 0.1 | 0.065 | 0.065 | 0.035 | 0.065
9 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
10 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
11 | 0.035 | 0.035 | 0.035 | 0.05 | 0.05 | 0.035 | 0.05
12 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
13 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
14 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
15 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
16 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
17 | 0.035 | 0.05 | 0.09 | 0.035 | 0.035 | 0.035 | 0.09
18 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
19 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
20 | 0.035 | 0.035 | 0.035 | 0.035 | 0.04 | 0.035 | 0.04
21 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
22 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
23 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
24 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
25 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
26 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
27 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
28 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
29 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
30 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
31 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Dan Perkins
[5 empty] | SIGNATURE: |  |  | 2025-06-06
[5 empty] | PHONE #: (541) 941-3951 |  |  | CERT #: 2339
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Anglers Cove SCHWC |  | ID#: 41 | 01483 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1800 | 1.2 | 90 | 108 | 12.4 | 7.56 | 40.996 | YES | 20
1900 | 1.2 | 90 | 108 | 12.3 | 7.49 | 40.2707 | YES | 20
1500 | 1.2 | 90 | 108 | 12.1 | 7.47 | 40.5173 | YES | 20
1215 | 1.2 | 90 | 108 | 12 | 7.49 | 41.0685 | YES | 20
1745 | 1.2 | 90 | 108 | 12.2 | 7.53 | 41.1039 | YES | 20
1800 | 1.2 | 90 | 108 | 12.4 | 7.56 | 40.996 | YES | 20
1800 | 1.2 | 90 | 108 | 12.4 | 7.54 | 40.7111 | YES | 20
1900 | 1.2 | 90 | 108 | 12.5 | 7.56 | 40.4887 | YES | 20
1715 | 1.2 | 90 | 108 | 12.5 | 7.58 | 40.788 | YES | 20
1445 | 1.2 | 90 | 108 | 12.6 | 7.59 | 40.668 | YES | 20
1800 | 1.2 | 90 | 108 | 12.4 | 7.53 | 40.5695 | YES | 20
1815 | 1.2 | 90 | 108 | 12.1 | 7.41 | 39.6803 | YES | 20
1715 | 1.2 | 90 | 108 | 12 | 7.4 | 39.8014 | YES | 20
1800 | 1.2 | 90 | 108 | 12 | 7.41 | 39.94 | YES | 20
1900 | 1.2 | 90 | 108 | 11.8 | 7.37 | 39.9057 | YES | 20
1830 | 1.2 | 90 | 108 | 11.9 | 7.38 | 39.7843 | YES | 20
1700 | 1.2 | 90 | 108 | 11.8 | 7.34 | 39.4919 | YES | 20
1900 | 1.2 | 90 | 108 | 12 | 7.36 | 39.2523 | YES | 20
1730 | 1.2 | 90 | 108 | 12.1 | 7.47 | 40.5173 | YES | 20
1930 | 1.2 | 90 | 108 | 12.2 | 7.5 | 40.6761 | YES | 20
1845 | 1.2 | 90 | 108 | 12.2 | 7.47 | 40.2534 | YES | 20
2000 | 1.2 | 90 | 108 | 12.4 | 7.53 | 40.5695 | YES | 20
1800 | 1.2 | 90 | 108 | 12.5 | 7.54 | 40.1916 | YES | 20
1800 | 1.2 | 90 | 108 | 13.1 | 7.56 | 38.9089 | YES | 20
1800 | 1.2 | 90 | 108 | 13 | 7.61 | 39.8962 | YES | 20
1700 | 1.2 | 90 | 108 | 13.1 | 7.6 | 39.4866 | YES | 20
1800 | 1.2 | 90 | 108 | 13.5 | 7.63 | 38.8799 | YES | 20
1800 | 1.2 | 90 | 108 | 13.4 | 7.62 | 38.9948 | YES | 20
1830 | 1.2 | 90 | 108 | 13.5 | 7.65 | 39.1675 | YES | 20
1145 | 1.2 | 90 | 108 | 13.4 | 7.57 | 38.2826 | YES | 20
1500 | 1.2 | 90 | 108 | 13.4 | 7.58 | 38.424 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2