## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Jackson
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-07-01
System Name: | Anglers Cove SCHWC |  |  | ID#: 41 | 01483 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
2 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
3 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
4 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
5 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
6 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
7 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
8 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
9 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
10 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
11 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
12 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
13 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
14 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
15 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
16 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
17 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
18 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
19 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
20 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
21 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
22 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
23 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
24 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
25 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
26 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
27 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
28 | 0.035 | 0.035 | 0.04 | 0.06 | 0.05 | 0.045 | 0.06
29 | 0.035 | 0.035 | 0.04 | 0.035 | 0.04 | 0.045 | 0.045
30 | 0.04 | 0.05 | 0.035 | 0.035 | 0.05 | 0.05 | 0.05
31 | 0.04 | OFF | 0.035 | 0.04 | 0.045 | 0.035 | 0.045
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Dan Perkins
[5 empty] | SIGNATURE: |  |  | 2025-08-03
[5 empty] | PHONE #: (541) 941-3951 |  |  | CERT #: 2339
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Anglers Cove SCHWC |  | ID#: 41 | 01483 | Month/Year: | 2025-07-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1730 | 1.2 | 90 | 108 | 15.3 | 7.56 | 33.6157 | YES | 20
1745 | 1.2 | 90 | 108 | 15.2 | 7.57 | 33.9655 | YES | 20
1900 | 1.2 | 90 | 108 | 15 | 7.54 | 34.0411 | YES | 20
1230 | 1.2 | 90 | 108 | 14.8 | 7.49 | 33.8655 | YES | 20
1800 | 1.2 | 90 | 108 | 15.2 | 7.51 | 33.2203 | YES | 20
1700 | 1.2 | 90 | 108 | 15.3 | 7.56 | 33.6157 | YES | 20
1730 | 1.2 | 90 | 108 | 15.5 | 7.58 | 33.4172 | YES | 20
1730 | 1.2 | 90 | 108 | 15.6 | 7.58 | 33.1954 | YES | 20
1730 | 1.2 | 90 | 108 | 15.5 | 7.57 | 33.2939 | YES | 20
1730 | 1.2 | 90 | 108 | 15.5 | 7.57 | 33.2939 | YES | 20
1730 | 1.2 | 90 | 108 | 15.6 | 7.58 | 33.1954 | YES | 20
1800 | 1.2 | 90 | 108 | 15.8 | 7.6 | 32.9994 | YES | 20
1100 | 1.2 | 90 | 108 | 15.5 | 7.56 | 33.1709 | YES | 20
1915 | 1.2 | 90 | 108 | 15.9 | 7.6 | 32.7803 | YES | 20
1700 | 1.2 | 90 | 108 | 15.9 | 7.61 | 32.9018 | YES | 20
1445 | 1.2 | 90 | 108 | 16 | 7.6 | 32.5626 | YES | 20
1530 | 1.2 | 90 | 108 | 15.9 | 7.6 | 32.7803 | YES | 20
1530 | 1.2 | 90 | 108 | 15.8 | 7.61 | 33.1217 | YES | 20
1900 | 1.2 | 90 | 108 | 16 | 7.63 | 32.9261 | YES | 20
2000 | 1.2 | 90 | 108 | 15.6 | 7.56 | 32.9507 | YES | 20
1815 | 1.2 | 90 | 108 | 15.8 | 7.55 | 32.3945 | YES | 20
1745 | 1.2 | 90 | 108 | 15.7 | 7.53 | 32.3706 | YES | 20
1815 | 1.2 | 90 | 108 | 15.7 | 7.52 | 32.251 | YES | 20
1945 | 1.2 | 90 | 108 | 15.7 | 7.53 | 32.3706 | YES | 20
1630 | 1.2 | 90 | 108 | 15.4 | 7.49 | 32.5389 | YES | 20
1845 | 1.2 | 90 | 108 | 15.6 | 7.56 | 32.9507 | YES | 20
1300 | 1.2 | 90 | 108 | 15.4 | 7.53 | 33.0241 | YES | 20
1815 | 1.2 | 90 | 108 | 15.6 | 7.56 | 32.9507 | YES | 20
1845 | 1.2 | 90 | 108 | 15.7 | 7.56 | 32.732 | YES | 20
1845 | 1.2 | 90 | 108 | 15.7 | 7.58 | 32.9751 | YES | 20
1815 | 1.2 | 90 | 108 | 15.6 | 7.53 | 32.587 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2