## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Jackson
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-08-01
System Name: | Anglers Cove SCHWC |  |  | ID#: 41 | 01483 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
2 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
3 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
4 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
5 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
6 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
7 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
8 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
9 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
10 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
11 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
12 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
13 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
14 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
15 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
16 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
17 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
18 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
19 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
20 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
21 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
22 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
23 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.05 | 0.05
24 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
25 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
26 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
27 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
28 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
29 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
30 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
31 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Dan Perkins
[5 empty] | SIGNATURE: |  |  | 2025-09-06
[5 empty] | PHONE #: (541) 941-3951 |  |  | CERT #: 2339
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Anglers Cove SCHWC |  | ID#: 41 | 01483 | Month/Year: | 2025-08-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
2200 | 1.2 | 90 | 108 | 15 | 7.5 | 33.5414 | YES | 20
1100 | 1.2 | 90 | 108 | 14.8 | 7.43 | 33.1224 | YES | 20
1800 | 1.2 | 90 | 108 | 13.9 | 7.49 | 35.9549 | YES | 20
1815 | 1.2 | 90 | 108 | 13.8 | 7.47 | 35.9284 | YES | 20
1715 | 1.2 | 90 | 108 | 13.8 | 7.48 | 36.0613 | YES | 20
1730 | 1.2 | 90 | 108 | 13.7 | 7.47 | 36.168 | YES | 20
1830 | 1.2 | 90 | 108 | 13.7 | 7.47 | 36.168 | YES | 20
1700 | 1.2 | 90 | 108 | 13.8 | 7.48 | 36.0613 | YES | 20
1230 | 1.2 | 90 | 108 | 13.7 | 7.46 | 36.0348 | YES | 20
1100 | 1.2 | 90 | 108 | 13.6 | 7.43 | 35.8756 | YES | 20
1800 | 1.2 | 90 | 108 | 14 | 7.49 | 35.7167 | YES | 20
1800 | 1.2 | 90 | 108 | 14.1 | 7.56 | 36.4089 | YES | 20
1800 | 1.2 | 90 | 108 | 14 | 7.51 | 35.9814 | YES | 20
1715 | 1.2 | 90 | 108 | 14 | 7.52 | 36.1145 | YES | 20
1930 | 1.2 | 90 | 108 | 14 | 7.53 | 36.248 | YES | 20
1430 | 1.2 | 90 | 108 | 13.8 | 7.49 | 36.1947 | YES | 20
1230 | 1.2 | 90 | 108 | 13.9 | 7.5 | 36.0879 | YES | 20
1900 | 1.2 | 90 | 108 | 13.8 | 7.5 | 36.3285 | YES | 20
1815 | 1.2 | 90 | 108 | 13.9 | 7.51 | 36.2213 | YES | 20
1915 | 1.2 | 90 | 108 | 14 | 7.52 | 36.1145 | YES | 20
1745 | 1.2 | 90 | 108 | 14.1 | 7.54 | 36.1411 | YES | 20
1700 | 1.2 | 90 | 108 | 14.7 | 7.56 | 34.985 | YES | 20
1400 | 1.2 | 90 | 108 | 15.2 | 7.58 | 34.0913 | YES | 20
1330 | 1.2 | 90 | 108 | 15.3 | 7.56 | 33.6157 | YES | 20
1830 | 1.2 | 90 | 108 | 15.6 | 7.56 | 32.9507 | YES | 20
2000 | 1.2 | 90 | 108 | 15.5 | 7.54 | 32.9264 | YES | 20
1800 | 1.2 | 90 | 108 | 15.4 | 7.54 | 33.1465 | YES | 20
1745 | 1.2 | 90 | 108 | 15.2 | 7.51 | 33.2203 | YES | 20
730 | 1.2 | 90 | 108 | 14.5 | 7.43 | 33.7907 | YES | 20
848 | 1.2 | 90 | 108 | 14 | 7.4 | 34.5488 | YES | 20
1700 | 1.2 | 90 | 108 | 14.6 | 7.5 | 34.4464 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2