## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-02-02
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 51 | 50 | 1 | 15 | 0.3
2 | 48 | 48 | 0 | 15 | 0.49
3 | 51 | 50 | 1 | 15 | 0.42
4 | 50 | 49 | 1 | 15 | 0.61
5 | 53 | 52 | 1 | 15 | 0.33
6 | 53 | 52 | 1 | 15 | 0.34
7 | 52 | 50 | 2 | 15 | 0.65
8 | 53 | 51 | 2 | 15 | 0.58
9 | 54 | 52 | 2 | 15 | 0.57
10 | 54 | 53 | 1 | 15 | 0.51
11 | 53 | 52 | 1 | 15 | 0.46
12 | 53 | 52 | 1 | 15 | 0.54
13 | 48 | 47 | 1 | 15 | 0.27
14 | 48 | 47 | 1 | 15 | 0.36
15 | 48 | 47 | 1 | 15 | 0.32
16 | 47 | 46 | 1 | 15 | 0.28
17 | 36 | 36 | 0 | 15 | 0.49
18 | 48 | 48 | 0 | 15 | 0.45
19 | 56 | 54 | 2 | 15 | 0.4
20 | 56 | 54 | 2 | 15 | 0.38
21 | 55 | 54 | 1 | 15 | 0.28
22 | 47 | 46 | 1 | 15 | 0.28
23 | 56 | 54 | 2 | 15 | 0.36
24 | 53 | 52 | 1 | 15 | 0.34
25 | 54 | 52 | 2 | 15 | 0.44
26 | 55 | 53 | 2 | 15 | 0.5
27 | 22 | 21 | 1 | 15 | 0.41
28 | 44 | 45 | -1 | 15 | 0.42
29
30
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 3-02-23
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2023-02-02
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 8% 16%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 5 | 906 | y | 3326 | 0 | 0%
2 | 4.5 | 864 | y | 2074 | 0 | 0%
3 | 4 | 878 | y | 2005 | 0 | 0%
4 | 4.5 | 882 | y | 2225 | 0 | 0%
5 | 5.5 | 927 | y | 3328 | 0 | 0%
6 | 4 | 870 | y | 1350 | 0 | 0%
7 | 4 | 880 | y | 2600 | 0 | 0%
8 | 4.5 | 892 | y | 2870 | 0 | 0%
9 | 5 | 912 | y | 2430 | 0 | 0%
10 | 5 | 918 | y | 2336 | 0 | 0%
11 | 4.5 | 874 | y | 2450 | 0 | 0%
12 | 4.5 | 841 | y | 2840 | 0 | 0%
13 | 4.5 | 930 | y | 3147 | 0 | 0%
14 | 4.5 | 885 | y | 2462 | 0 | 0%
15 | 4 | 876 | y | 2598 | 0 | 0%
16 | 4 | 904 | y | 2584 | 0 | 0%
17 | 3.5 | 940 | y | 2098 | 0 | 0%
18 | 4 | 908 | y | 2575 | 0 | 0%
19 | 4 | 914 | y | 2313 | 0 | 0%
20 | 4.5 | 883 | y | 3060 | 0 | 0%
21 | 5 | 910 | y | 2534 | 0 | 0%
22 | 4 | 843 | y | 2014 | 0 | 0%
23 | 3.5 | 845 | y | 2084 | 0 | 0%
24 | 4 | 911 | y | 2914 | 0 | 0%
25 | 16.5 | 398 | y | 5629 | 0 | 0%
26 | 16 | 385 | y | 2810 | 0 | 0%
27 | 12 | 509 | y | 2133 | 0 | 0%
28 | 14.5 | 415 | y | 2603 | 0 | 0%
29 |  |  |  |  | 0 | #DIV/0!
30 |  |  |  |  | 0 | #DIV/0!
31 |  |  |  |  | 0 | #DIV/0!
73392
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2023-03-02
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).