## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-03-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 49 | 48 | 1 | 15 | 0.14
2 | 36 | 35 | 1 | 15 | 0.12
3 | 49 | 49 | 0 | 15 | 0.13
4 | 49 | 49 | 0 | 15 | 0.21
5 | 50 | 49 | 1 | 15 | 0.12
6 | 51 | 50 | 1 | 15 | 0.11
7 | 37 | 36 | 1 | 15 | 0.14
8 | 37 | 36 | 1 | 15 | 0.28
9 | 37 | 36 | 1 | 15 | 0.26
10 | 37 | 36 | 1 | 15 | 0.21
11 | 36 | 36 | 0 | 15 | 0.16
12 | 53 | 53 | 0 | 15 | 0.16
13 | 53 | 53 | 0 | 15 | 0.24
14 | 37 | 35 | 2 | 15 | 0.25
15 | 53 | 53 | 0 | 15 | 0.49
16 | 53 | 53 | 0 | 15 | 0.19
17 | 41 | 41 | 0 | 15 | 0.14
18 | 37 | 35 | 2 | 15 | 0.2
19 | 45 | 45 | 0 | 15 | 0.18
20 | 54 | 54 | 0 | 15 | 0.14
21 | 41 | 41 | 0 | 15 | 0.24
22 | 36 | 35 | 1 | 15 | 0.26
23 | 35 | 34 | 1 | 15 | 0.35
24 | 45 | 45 | 0 | 15 | 0.23
25 | 54 | 54 | 0 | 15 | 0.16
26 | 41 | 41 | 0 | 15 | 0.11
27 | 36 | 35 | 1 | 15 | 0.16
28 | 54 | 54 | 0 | 15 | 0.12
29 | 34 | 33 | 1 | 15 | 0.1
30 | 35 | 34 | 1 | 15 | 0.34
31 | 34 | 33 | 1 | 15 | 0.23
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 04-02-24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2024-03-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 9.5 | 526 | y | 2664 | 0 | 0%
2 | 10 | 503 | y | 1638 | 0 | 0%
3 | 10 | 549 | y | 2958 | 0 | 0%
4 | 10 | 486 | y | 2741 | 0 | 0%
5 | 9.5 | 523 | y | 2225 | 0 | 0%
6 | 10.5 | 506 | y | 1920 | 0 | 0%
7 | 9.5 | 519 | y | 2752 | 0 | 0%
8 | 9.5 | 496 | y | 1501 | 0 | 0%
9 | 9.5 | 508 | y | 2640 | 0 | 0%
10 | 9.5 | 510 | y | 2317 | 0 | 0%
11 | 9 | 537 | y | 3520 | 0 | 0%
12 | 11 | 446 | y | 2500 | 0 | 0%
13 | 10 | 476 | y | 2336 | 0 | 0%
14 | 9.5 | 530 | y | 2280 | 0 | 0%
15 | 10.5 | 450 | y | 2340 | 0 | 0%
16 | 10.5 | 455 | y | 2183 | 0 | 0%
17 | 9.5 | 520 | y | 3050 | 0 | 0%
18 | 9.5 | 525 | y | 2742 | 0 | 0%
19 | 9.5 | 528 | y | 3480 | 0 | 0%
20 | 9.5 | 518 | y | 2259 | 0 | 0%
21 | 10 | 525 | y | 1899 | 0 | 0%
22 | 9.5 | 528 | y | 2349 | 0 | 0%
23 | 9 | 541 | y | 3170 | 0 | 0%
24 | 9 | 529 | y | 1897 | 0 | 0%
25 | 10 | 481 | y | 2980 | 0 | 0%
26 | 8.5 | 556 | y | 2460 | 0 | 0%
27 | 9 | 540 | y | 2606 | 0 | 0%
28 | 11 | 378 | y | 2246 | 0 | 0%
29 | 9.5 | 493 | y | 3024 | 0 | 0%
30 | 9 | 538 | y | 2477 | 0 | 0%
31 | 10 | 508 | y | 3096 | 0 | 0%
78250
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2024-04-02
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).