## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-07-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 41 | 35 | 6 | 15 | 0.25
2 | 42 | 35 | 7 | 15 | 0.3
3 | 41 | 34 | 7 | 15 | 0.32
4 | 42 | 35 | 7 | 15 | 0.27
5 | 40 | 32 | 8 | 15 | 0.38
6 | 41 | 34 | 7 | 15 | 0.31
7 | 38 | 35 | 3 | 15 | 0.2
8 | 41 | 34 | 7 | 15 | 0.18
9 | 41 | 35 | 6 | 15 | 0.2
10 | 41 | 34 | 7 | 15 | 0.16
11 | 41 | 35 | 6 | 15 | 0.27
12 | 41 | 35 | 6 | 15 | 0.24
13 | 41 | 35 | 6 | 15 | 0.27
14 | 41 | 35 | 6 | 15 | 0.23
15 | 41 | 35 | 6 | 15 | 0.17
16 | 41 | 35 | 6 | 15 | 0.29
17 | 42 | 35 | 7 | 15 | 0.25
18 | 41 | 34 | 7 | 15 | 0.42
19 | 42 | 34 | 8 | 15 | 0.14
20 | 48 | 42 | 6 | 15 | 0.17
21 | 48 | 41 | 7 | 15 | 0.12
22 | 48 | 41 | 7 | 15 | 0.16
23 | 48 | 42 | 6 | 15 | 0.19
24 | 48 | 42 | 6 | 15 | 0.2
25 | 48 | 42 | 6 | 15 | 0.18
26 | 48 | 42 | 6 | 15 | 0.24
27 | 43 | 35 | 8 | 15 | 0.12
28 | 48 | 42 | 6 | 15 | 0.16
29 | 48 | 42 | 6 | 15 | 0.18
30 | 48 | 42 | 5 | 15 | 0.12
31 | 42 | 34 | 0 | 15 | 0.3
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 08-02-24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2024-07-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 9 | 481 | y | 8078 | 0 | 0%
2 | 9.5 | 461 | y | 7486 | 0 | 0%
3 | 9.5 | 454 | y | 7469 | 0 | 0%
4 | 9.5 | 450 | y | 9608 | 0 | 0%
5 | 12 | 357 | y | 8957 | 0 | 0%
6 | 9.5 | 429 | y | 4941 | 0 | 0%
7 | 9.5 | 428 | y | 7539 | 0 | 0%
8 | 10 | 404 | y | 8606 | 0 | 0%
9 | 9.5 | 415 | y | 11123 | 0 | 0%
10 | 10 | 391 | y | 5342 | 0 | 0%
11 | 10 | 383 | y | 11264 | 0 | 0%
12 | 10 | 385 | y | 8774 | 0 | 0%
13 | 9.5 | 382 | y | 8810 | 0 | 0%
14 | 9 | 385 | y | 7640 | 0 | 0%
15 | 9.5 | 364 | y | 9140 | 0 | 0%
16 | 9 | 380 | y | 7730 | 0 | 0%
17 | 9.5 | 350 | y | 8880 | 0 | 0%
18 | 9.5 | 360 | y | 8017 | 0 | 0%
19 | 9.5 | 347 | y | 7574 | 0 | 0%
20 | 7.5 | 412 | y | 8309 | 0 | 0%
21 | 7.5 | 400 | y | 9093 | 0 | 0%
22 | 7.5 | 391 | y | 8131 | 0 | 0%
23 | 8 | 374 | y | 7704 | 0 | 0%
24 | 7.5 | 382 | y | 8179 | 0 | 0%
25 | 8 | 348 | y | 10902 | 0 | 0%
26 | 6.5 | 362 | y | 8370 | 0 | 0%
27 | 7.5 | 390 | y | 9329 | 0 | 0%
28 | 7.5 | 350 | y | 6341 | 0 | 0%
29 | 8 | 328 | y | 8750 | 0 | 0%
30 | 8 | 325 | y | 7730 | 0 | 0%
31 | 9.5 | 520 |  | 5300 | 0 | 0%
255116
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2024-08-02
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%