## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-08-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 41 | 34 | 7 | 15 | 0.26
2 | 40 | 34 | 6 | 15 | 0.24
3 | 41 | 34 | 7 | 15 | 0.27
4 | 42 | 35 | 7 | 15 | 0.21
5 | 41 | 32 | 9 | 15 | 0.27
6 | 39 | 32 | 7 | 15 | 0.18
7 | 40 | 32 | 8 | 15 | 0.13
8 | 38 | 32 | 6 | 15 | 0.3
9 | 41 | 33 | 8 | 15 | 0.17
10 | 41 | 33 | 8 | 15 | 0.11
11 | 41 | 32 | 9 | 15 | 0.13
12 | 41 | 33 | 8 | 15 | 0.26
13 | 44 | 40 | 4 | 15 | 0.17
14 | 41 | 32 | 9 | 15 | 0.12
15 | 42 | 33 | 9 | 15 | 0.11
16 | 41 | 32 | 9 | 15 | 0.24
17 | 42 | 33 | 9 | 15 | 0.11
18 | 42 | 32 | 10 | 15 | 0.12
19 | 54 | 50 | 4 | 15 | 0.13
20 | 56 | 52 | 4 | 15 | 0.24
21 | 40 | 32 | 8 | 15 | 0.11
22 | 52 | 47 | 5 | 15 | 0.12
23 | 55 | 50 | 5 | 15 | 0.13
24 | 38 | 28 | 10 | 15 | 0.31
25 | 37 | 25 | 12 | 15 | 0.34
26 | 41 | 31 | 10 | 15 | 0.37
27 | 40 | 31 | 9 | 15 | 0.35
28 | 40 | 30 | 10 | 15 | 0.36
29 | 41 | 31 | 10 | 15 | 0.15
30 | 41 | 32 | 5 | 15 | 0.16
31 | 41 | 32 | 9 | 15 | 0.14
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 09-04-24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2024-08-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 10 | 487 | y | 9030 | 0 | 0%
2 | 10.5 | 471 | y | 6170 | 0 | 0%
3 | 9.5 | 501 | y | 7536 | 0 | 0%
4 | 10 | 479 | y | 7700 | 0 | 0%
5 | 11 | 430 | y | 7474 | 0 | 0%
6 | 11 | 420 | y | 7519 | 0 | 0%
7 | 10 | 460 | y | 7164 | 0 | 0%
8 | 12 | 400 | y | 9009 | 0 | 0%
9 | 9.5 | 467 | y | 8373 | 0 | 0%
10 | 10 | 444 | y | 6592 | 0 | 0%
11 | 10 | 447 | y | 6545 | 0 | 0%
12 | 9.5 | 451 | y | 8974 | 0 | 0%
13 | 10 | 428 | y | 8713 | 0 | 0%
14 | 9.5 | 446 | y | 6230 | 0 | 0%
15 | 10 | 417 | y | 7510 | 0 | 0%
16 | 9.5 | 434 | y | 6710 | 0 | 0%
17 | 10 | 402 | y | 7900 | 0 | 0%
18 | 10.5 | 388 | y | 5908 | 0 | 0%
19 | 10 | 394 | y | 8115 | 0 | 0%
20 | 10.5 | 363 | y | 7459 | 0 | 0%
21 | 10 | 378 | y | 7603 | 0 | 0%
22 | 10 | 379 | y | 7099 | 0 | 0%
23 | 10 | 367 | y | 5529 | 0 | 0%
24 | 12 | 357 | y | 6206 | 0 | 0%
25 | 13.5 | 282 | y | 4910 | 0 | 0%
26 | 10 | 366 | y | 8325 | 0 | 0%
27 | 10 | 361 | y | 5707 | 0 | 0%
28 | 10.5 | 337 | y | 8008 | 0 | 0%
29 | 10 | 353 | y | 6222 | 0 | 0%
30 | 10 | 350 | y | 6930 | 0 | 0%
31 | 10 | 348 |  | 9092 | 0 | 0%
226262
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2024-09-04
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%