## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-08-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 41 | 32 | 9 | 15 | 0.14
2 | 40 | 31 | 9 | 15 | 0.13
3 | 41 | 32 | 9 | 15 | 0.14
4 | 41 | 31 | 10 | 15 | 0.11
5 | 54 | 50 | 4 | 15 | 0.19
6 | 41 | 32 | 9 | 15 | 0.1
7 | 34 | 22 | 12 | 15 | 0.25
8 | 59 | 54 | 5 | 15 | 0.11
9 | 40 | 30 | 10 | 15 | 0.21
10 | 40 | 31 | 9 | 15 | 0.17
11 | 57 | 52 | 5 | 15 | 0.16
12 | 38 | 30 | 8 | 15 | 0.28
13 | 39 | 29 | 10 | 15 | 0.18
14 | 41 | 32 | 9 | 15 | 0.12
15 | 43 | 33 | 10 | 15 | 0.15
16 | 40 | 31 | 9 | 15 | 0.14
17 | 42 | 32 | 10 | 15 | 0.14
18 | 40 | 32 | 8 | 15 | 0.21
19 | 41 | 32 | 9 | 15 | 0.19
20 | 40 | 32 | 8 | 15 | 0.18
21 | 41 | 32 | 9 | 15 | 0.22
22 | 40 | 32 | 8 | 15 | 0.17
23 | 36 | 24 | 12 | 15 | 0.31
24 | 38 | 26 | 12 | 15 | 0.28
25 | 36 | 25 | 11 | 15 | 0.31
26 | 37 | 27 | 10 | 15 | 0.28
27 | 40 | 30 | 10 | 15 | 0.21
28 | 40 | 31 | 9 | 15 | 0.22
29 | 40 | 31 | 9 | 15 | 0.21
30 | 40 | 30 | 5 | 15 | 0.17
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 10-04-24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2024-09-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 10 | 333 | y | 6809 | 0 | 0%
2 | 10 | 335 | y | 7588 | 0 | 0%
3 | 10 | 323 | y | 9209 | 0 | 0%
4 | 10 | 326 | y | 7260 | 0 | 0%
5 | 9.5 | 328 | y | 9849 | 0 | 0%
6 | 9.5 | 325 | y | 7084 | 0 | 0%
7 | 12.5 | 262 | y | 7960 | 0 | 0%
8 | 11 | 270 | y | 5832 | 0 | 0%
9 | 12 | 260 | y | 8552 | 0 | 0%
10 | 10.5 | 285 | y | 7282 | 0 | 0%
11 | 8 | 300 | y | 7554 | 0 | 0%
12 | 10 | 440 | y | 6381 | 0 | 0%
13 | 11.5 | 429 | y | 4791 | 0 | 0%
14 | 10.5 | 454 | y | 4981 | 0 | 0%
15 | 10 | 462 | y | 5190 | 0 | 0%
16 | 10.5 | 458 | y | 6639 | 0 | 0%
17 | 10 | 455 | y | 5289 | 0 | 0%
18 | 10 | 449 | y | 6430 | 0 | 0%
19 | 10.5 | 429 | y | 5982 | 0 | 0%
20 | 10 | 446 | y | 7286 | 0 | 0%
21 | 10 | 430 | y | 8350 | 0 | 0%
22 | 9.5 | 457 | y | 4419 | 0 | 0%
23 | 12.5 | 361 | y | 7349 | 0 | 0%
24 | 12 | 352 | y | 4719 | 0 | 0%
25 | 12 | 356 | y | 6690 | 0 | 0%
26 | 12 | 352 | y | 4760 | 0 | 0%
27 | 10 | 394 | y | 5909 | 0 | 0%
28 | 10.5 | 399 | y | 2588 | 0 | 0%
29 | 11 | 363 | y | 5047 | 0 | 0%
30 | 11 | 355 | y | 6202 | 0 | 0%
31 |  |  |  |  | 0 | #DIV/0!
193981
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2024-10-04
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%