## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-10-01
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 41 | 31 | 10 | 15 | 0.13
2 | 41 | 32 | 9 | 15 | 0.16
3 | 41 | 32 | 9 | 15 | 0.13
4 | 41 | 32 | 9 | 15 | 0.13
5 | 41 | 32 | 9 | 15 | 0.18
6 | 41 | 31 | 10 | 15 | 0.2
7 | 42 | 33 | 9 | 15 | 0.43
8 | 40 | 30 | 10 | 15 | 0.41
9 | 40 | 30 | 10 | 15 | 0.25
10 | 42 | 32 | 10 | 15 | 0.26
11 | 40 | 31 | 9 | 15 | 0.22
12 | 41 | 32 | 9 | 15 | 0.22
13 | 56 | 51 | 5 | 15 | 0.28
14 | 9 | 3 | 6 | 15 | 0.24
15 | 45 | 36 | 9 | 15 | 0.22
16 | 40 | 31 | 9 | 15 | 0.34
17 | 45 | 35 | 10 | 15 | 0.29
18 | 40 | 30 | 10 | 15 | 0.18
19 | 52 | 48 | 4 | 15 | 0.15
20 | 40 | 31 | 9 | 15 | 0.13
21 | 58 | 54 | 4 | 15 | 0.14
22 | 40 | 31 | 9 | 15 | 0.14
23 | 40 | 30 | 10 | 15 | 0.16
24 | 39 | 30 | 9 | 15 | 0.17
25 | 40 | 30 | 10 | 15 | 0.16
26 | 45 | 36 | 9 | 15 | 0.17
27 | 40 | 30 | 10 | 15 | 0.18
28 | 40 | 31 | 9 | 15 | 0.25
29 | 40 | 32 | 8 | 15 | 0.23
30 | 42 | 32 | 5 | 15 | 0.2
31 | 40 | 32 | 8 | 15 | 0.2
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 11-02-24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2024-10-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 10 | 401 | y | 6126 | 0 | 0%
2 | 10.5 | 376 | y | 4403 | 0 | 0%
3 | 10 | 394 | y | 5844 | 0 | 0%
4 | 10 | 385 | y | 6090 | 0 | 0%
5 | 10 | 328 | y | 1200 | 0 | 0%
6 | 10 | 387 | y | 7809 | 0 | 0%
7 | 10 | 380 | y | 4396 | 0 | 0%
8 | 11 | 350 | y | 5220 | 0 | 0%
9 | 11 | 340 | y | 5241 | 0 | 0%
10 | 10 | 370 | y | 5874 | 0 | 0%
11 | 10 | 378 | y | 2966 | 0 | 0%
12 | 10.5 | 355 | y | 4200 | 0 | 0%
13 | 10 | 368 | y | 4340 | 0 | 0%
14 | 10 | 358 | y | 4246 | 0 | 0%
15 | 9 | 409 | y | 4700 | 0 | 0%
16 | 11 | 339 | y | 3221 | 0 | 0%
17 | 10.5 | 354 | y | 4154 | 0 | 0%
18 | 11 | 338 | y | 2630 | 0 | 0%
19 | 10.5 | 343 | y | 4633 | 0 | 0%
20 | 10.5 | 350 | y | 3845 | 0 | 0%
21 | 12 | 304 | y | 5371 | 0 | 0%
22 | 10.5 | 345 | y | 2649 | 0 | 0%
23 | 10.5 | 344 | y | 3256 | 0 | 0%
24 | 10 | 357 | y | 2680 | 0 | 0%
25 | 11 | 300 | y | 2460 | 0 | 0%
26 | 11 | 319 | y | 2091 | 0 | 0%
27 | 10.5 | 347 | y | 2089 | 0 | 0%
28 | 10.5 | 332 | y | 2612 | 0 | 0%
29 | 10 | 352 | y | 2250 | 0 | 0%
30 | 10.5 | 341 | y | 2440 | 0 | 0%
31 | 10 | 350 |  | 2560 | 0 | 0%
121596
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2024-11-02
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%