## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-11-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 31 | 9 | 15 | 0.17
2 | 40 | 30 | 10 | 15 | 0.26
3 | 41 | 33 | 8 | 15 | 0.19
4 | 43 | 34 | 9 | 15 | 0.23
5 | 40 | 31 | 9 | 15 | 0.26
6 | 43 | 35 | 8 | 15 | 0.2
7 | 40 | 31 | 9 | 15 | 0.18
8 | 44 | 35 | 9 | 15 | 0.24
9 | 43 | 34 | 9 | 15 | 0.28
10 | 40 | 31 | 9 | 15 | 0.24
11 | 40 | 31 | 9 | 15 | 0.34
12 | 39 | 29 | 10 | 15 | 0.26
13 | 39 | 31 | 8 | 15 | 0.25
14 | 40 | 31 | 9 | 15 | 0.24
15 | 40 | 31 | 9 | 15 | 0.2
16 | 41 | 32 | 9 | 15 | 0.32
17 | 41 | 32 | 9 | 15 | 0.34
18 | 40 | 31 | 9 | 15 | 0.28
19 | 39 | 31 | 8 | 15 | 0.16
20 | 40 | 31 | 9 | 15 | 0.14
21 | 41 | 32 | 9 | 15 | 0.14
22 | 58 | 54 | 4 | 15 | 0.14
23 | 45 | 37 | 8 | 15 | 0.15
24 | 48 | 42 | 6 | 15 | 0.41
25 | 56 | 52 | 4 | 15 | 0.17
26 | 50 | 41 | 9 | 15 | 0.12
27 | 40 | 32 | 8 | 15 | 0.23
28 | 45 | 37 | 8 | 15 | 0.18
29 | 50 | 42 | 8 | 15 | 0.16
30 | 46 | 37 | 5 | 15 | 0.12
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 12-01-24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2024-11-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 10.5 | 336 | y | 2183 | 0 | 0%
2 | 10.5 | 341 | y | 2341 | 0 | 0%
3 | 10 | 349 | y | 3017 | 0 | 0%
4 | 10.5 | 333 | y | 2898 | 0 | 0%
5 | 10 | 348 | y | 2080 | 0 | 0%
6 | 11 | 316 | y | 3040 | 0 | 0%
7 | 10.5 | 328 | y | 1614 | 0 | 0%
8 | 11 | 315 | y | 2995 | 0 | 0%
9 | 10.5 | 323 | y | 2354 | 0 | 0%
10 | 10 | 348 | y | 1900 | 0 | 0%
11 | 10.5 | 319 | y | 2713 | 0 | 0%
12 | 10 | 328 | y | 2471 | 0 | 0%
13 | 10 | 338 | y | 1919 | 0 | 0%
14 | 10 | 330 | y | 2440 | 0 | 0%
15 | 10.5 | 323 | y | 1852 | 0 | 0%
16 | 10.5 | 330 | y | 2525 | 0 | 0%
17 | 10.5 | 315 | y | 2677 | 0 | 0%
18 | 10.5 | 310 | y | 2352 | 0 | 0%
19 | 10.5 | 320 | y | 3404 | 0 | 0%
20 | 10.5 | 272 | y | 3052 | 0 | 0%
21 | 10 | 394 | y | 2174 | 0 | 0%
22 | 12 | 376 | y | 1209 | 0 | 0%
23 | 8 | 396 | y | 2246 | 0 | 0%
24 | 8.5 | 376 | y | 2837 | 0 | 0%
25 | 9 | 346 | y | 3067 | 0 | 0%
26 | 9 | 347 | y | 2088 | 0 | 0%
27 | 8 | 387 | y | 2702 | 0 | 0%
28 | 9 | 348 | y | 3022 | 0 | 0%
29 | 8.5 | 360 | y | 3630 | 0 | 0%
30 | 8 | 376 | y | 2627 | 0 | 0%
31
75429
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2024-12-01
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%