## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-12-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 48 | 40 | 8 | 15 | 0.14
2 | 49 | 41 | 8 | 15 | 0.18
3 | 44 | 36 | 8 | 15 | 0.16
4 | 38 | 28 | 10 | 15 | 0.28
5 | 57 | 53 | 4 | 15 | 0.19
6 | 54 | 50 | 4 | 15 | 0.14
7 | 58 | 54 | 4 | 15 | 0.24
8 | 37 | 27 | 10 | 15 | 0.15
9 | 56 | 52 | 4 | 15 | 0.13
10 | 38 | 30 | 8 | 15 | 0.18
11 | 40 | 31 | 9 | 15 | 0.19
12 | 41 | 33 | 8 | 15 | 0.23
13 | 41 | 34 | 7 | 15 | 0.24
14 | 41 | 32 | 9 | 15 | 0.21
15 | 40 | 31 | 9 | 15 | 0.23
16 | 44 | 35 | 9 | 15 | 0.25
17 | 44 | 35 | 9 | 15 | 0.22
18 | 41 | 32 | 9 | 15 | 0.27
19 | 41 | 32 | 9 | 15 | 0.25
20 | 40 | 31 | 9 | 15 | 0.24
21 | 40 | 31 | 9 | 15 | 0.28
22 | 40 | 31 | 9 | 15 | 0.29
23 | 39 | 30 | 9 | 15 | 0.34
24 | 40 | 31 | 9 | 15 | 0.42
25 | 46 | 36 | 10 | 15 | 0.63
26 | 39 | 29 | 10 | 15 | 0.22
27 | 41 | 31 | 10 | 15 | 0.28
28 | 43 | 34 | 9 | 15 | 0.22
29 | 40 | 31 | 9 | 15 | 0.26
30 | 56 | 51 | 5 | 15 | 0.27
31 | 41 | 32 | 9 | 15 | 0.21
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 01/04/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2024-12-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 9 | 348 | y | 3359 | 0 | 0%
2 | 9 | 352 | y | 2428 | 0 | 0%
3 | 9 | 351 | y | 2549 | 0 | 0%
4 | 11.5 | 511 | y | 3110 | 0 | 0%
5 | 12 | 478 | y | 1930 | 0 | 0%
6 | 13 | 446 | y | 2837 | 0 | 0%
7 | 12.5 | 475 | y | 2232 | 0 | 0%
8 | 11 | 526 | y | 2318 | 0 | 0%
9 | 11.5 | 495 | y | 2549 | 0 | 0%
10 | 11 | 520 | y | 1959 | 0 | 0%
11 | 10.5 | 547 | y | 3264 | 0 | 0%
12 | 10 | 551 | y | 1328 | 0 | 0%
13 | 10 | 478 | y | 1740 | 0 | 0%
14 | 9.5 | 588 | y | 3720 | 0 | 0%
15 | 10 | 565 | y | 2459 | 0 | 0%
16 | 11 | 513 | y | 3010 | 0 | 0%
17 | 10 | 528 | y | 2653 | 0 | 0%
18 | 10 | 552 | y | 2688 | 0 | 0%
19 | 10.5 | 531 | y | 2703 | 0 | 0%
20 | 10.5 | 519 | y | 2537 | 0 | 0%
21 | 10 | 552 | y | 2214 | 0 | 0%
22 | 10.5 | 532 | y | 2407 | 0 | 0%
23 | 11 | 505 | y | 2871 | 0 | 0%
24 | 11.5 | 491 | y | 2779 | 0 | 0%
25 | 11.5 | 480 | y | 2594 | 0 | 0%
26 | 11.5 | 492 | y | 2192 | 0 | 0%
27 | 10 | 554 | y | 1735 | 0 | 0%
28 | 10.5 | 521 | y | 1669 | 0 | 0%
29 | 10.5 | 541 | y | 2664 | 0 | 0%
30 | 10 | 530 | y | 2598 | 0 | 0%
31 | 10.5 | 526 | y | 2990
78086
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2025-01-04
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%