## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-01-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 42 | 33 | 9 | 15 | 0.26
2 | 43 | 34 | 9 | 15 | 0.28
3 | 41 | 32 | 9 | 15 | 0.23
4 | 41 | 32 | 9 | 15 | 0.25
5 | 42 | 33 | 9 | 15 | 0.36
6 | 43 | 34 | 9 | 15 | 0.35
7 | 41 | 32 | 9 | 15 | 0.4
8 | 40 | 31 | 9 | 15 | 0.4
9 | 41 | 32 | 9 | 15 | 0.26
10 | 53 | 49 | 4 | 15 | 0.16
11 | 54 | 50 | 4 | 15 | 0.14
12 | 40 | 30 | 10 | 15 | 0.17
13 | 60 | 55 | 5 | 15 | 0.18
14 | 59 | 55 | 4 | 15 | 0.14
15 | 41 | 32 | 9 | 15 | 0.26
16 | 41 | 32 | 9 | 15 | 0.21
17 | 43 | 34 | 9 | 15 | 0.2
18 | 41 | 32 | 9 | 15 | 0.2
19 | 41 | 32 | 9 | 15 | 0.24
20 | 40 | 31 | 9 | 15 | 0.22
21 | 40 | 30 | 10 | 15 | 0.32
22 | 45 | 36 | 9 | 15 | 0.24
23 | 44 | 35 | 9 | 15 | 0.33
24 | 42 | 34 | 8 | 15 | 0.23
25 | 42 | 33 | 9 | 15 | 0.22
26 | 42 | 33 | 9 | 15 | 0.25
27 | 40 | 32 | 8 | 15 | 0.27
28 | 41 | 32 | 9 | 15 | 0.25
29 | 44 | 35 | 9 | 15 | 0.24
30 | 41 | 32 | 5 | 15 | 0.25
31 | 44 | 34 | 9 | 15 | 0.27
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 02/06/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2025-01-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 10.5 | 525 | y | 2188 | 0 | 0%
2 | 10.5 | 530 | y | 3058 | 0 | 0%
3 | 10.5 | 534 | y | 1975 | 0 | 0%
4 | 10.5 | 519 | y | 2316 | 0 | 0%
5 | 10.5 | 535 | y | 3732 | 0 | 0%
6 | 10 | 540 | y | 2258 | 0 | 0%
7 | 9.5 | 582 | y | 2410 | 0 | 0%
8 | 10 | 550 | y | 1691 | 0 | 0%
9 | 10.5 | 534 | y | 2055 | 0 | 0%
10 | 11.5 | 493 | y | 3840 | 0 | 0%
11 | 11.5 | 480 | y | 2246 | 0 | 0%
12 | 10.5 | 560 | y | 2736 | 0 | 0%
13 | 12 | 474 | y | 2808 | 0 | 0%
14 | 12 | 461 | y | 2606 | 0 | 0%
15 | 10.5 | 535 | y | 2289 | 0 | 0%
16 | 10.5 | 535 | y | 2160 | 0 | 0%
17 | 10.5 | 527 | y | 3034 | 0 | 0%
18 | 10.5 | 528 | y | 2105 | 0 | 0%
19 | 10.5 | 533 | y | 2361 | 0 | 0%
20 | 10.5 | 531 | y | 2665 | 0 | 0%
21 | 11.5 | 477 | y | 2602 | 0 | 0%
22 | 11 | 498 | y | 3080 | 0 | 0%
23 | 11 | 497 | y | 2400 | 0 | 0%
24 | 10.5 | 530 | y | 2322 | 0 | 0%
25 | 10 | 545 | y | 2430 | 0 | 0%
26 | 10 | 536 | y | 2608 | 0 | 0%
27 | 10 | 550 | y | 3168 | 0 | 0%
28 | 10 | 546 | y | 1753 | 0 | 0%
29 | 10.5 | 525 | y | 3648 | 0 | 0%
30 | 10 | 535 | y | 2076 | 0 | 0%
31 | 10.5 | 521 | y | 2539
79159
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2025-02-06
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%