## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-02-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 42 | 34 | 8 | 15 | 0.28
2 | 44 | 35 | 9 | 15 | 0.29
3 | 40 | 31 | 9 | 15 | 0.35
4 | 44 | 35 | 9 | 15 | 0.47
5 | 40 | 31 | 9 | 15 | 0.32
6 | 40 | 31 | 9 | 15 | 0.3
7 | 40 | 31 | 9 | 15 | 0.29
8 | 40 | 31 | 9 | 15 | 0.48
9 | 56 | 51 | 5 | 15 | 0.24
10 | 39 | 30 | 9 | 15 | 0.33
11 | 46 | 35 | 11 | 15 | 0.28
12 | 39 | 31 | 8 | 15 | 0.85
13 | 42 | 33 | 9 | 15 | 0.73
14 | 40 | 30 | 10 | 15 | 0.42
15 | 40 | 31 | 9 | 15 | 0.42
16 | 58 | 53 | 5 | 15 | 0.28
17 | 40 | 30 | 10 | 15 | 0.23
18 | 42 | 33 | 9 | 15 | 0.32
19 | 35 | 35 | 0 | 15 | 0.27
20 | 41 | 35 | 6 | 15 | 0.48
21 | 42 | 36 | 6 | 15 | 0.46
22 | 41 | 36 | 5 | 15 | 0.33
23 | 44 | 36 | 8 | 15 | 0.31
24 | 44 | 36 | 8 | 15 | 0.29
25 | 37 | 36 | 1 | 15 | 0.27
26 | 35 | 34 | 1 | 15 | 0.25
27 | 33 | 32 | 1 | 15 | 0.18
28 | 34 | 33 | 1 | 15 | 0.25
29
30
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 03/06/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2025-02-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 10 | 542 | y | 803 | 0 | 0%
2 | 10 | 549 | y | 2890 | 0 | 0%
3 | 10 | 530 | y | 2745 | 0 | 0%
4 | 11 | 487 | y | 2127 | 0 | 0%
5 | 10 | 532 | y | 2231 | 0 | 0%
6 | 10 | 537 | y | 1910 | 0 | 0%
7 | 10 | 528 | y | 2560 | 0 | 0%
8 | 10 | 518 | y | 2586 | 0 | 0%
9 | 9.5 | 549 | y | 2453 | 0 | 0%
10 | 9.5 | 555 | y | 4348 | 0 | 0%
11 | 10 | 530 | y | 3157 | 0 | 0%
12 | 10 | 525 | y | 1739 | 0 | 0%
13 | 10 | 523 | y | 2083 | 0 | 0%
14 | 10 | 515 | y | 2506 | 0 | 0%
15 | 10 | 523 | y | 2448 | 0 | 0%
16 | 11 | 470 | y | 2440 | 0 | 0%
17 | 10 | 520 | y | 2450 | 0 | 0%
18 | 10 | 508 | y | 2715 | 0 | 0%
19 | 10 | 545 | y | 2284 | 0 | 0%
20 | 10.5 | 498 | y | 2540 | 0 | 0%
21 | 10.5 | 520 | y | 2304 | 0 | 0%
22 | 11 | 471 | y | 3267 | 0 | 0%
23 | 11 | 540 | y | 2088 | 0 | 0%
24 | 11.5 | 543 | y | 3610 | 0 | 0%
25 | 11.5 | 461 | y | 3237 | 0 | 0%
26 | 10.5 | 508 | y | 1418 | 0 | 0%
27 | 11 | 482 | y | 2852 | 0 | 0%
28 | 10 | 526 | y | 2409 | 0 | 0%
29 |  |  |  |  | 0 | #DIV/0!
30 |  |  |  |  | 0 | #DIV/0!
31
70200
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2025-03-06
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%