## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-03-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 33 | 32 | 1 | 15 | 0.21
2 | 32 | 30 | 2 | 15 | 0.34
3 | 38 | 37 | 1 | 15 | 0.38
4 | 39 | 38 | 1 | 15 | 0.34
5 | 39 | 38 | 1 | 15 | 0.32
6 | 35 | 34 | 1 | 15 | 0.42
7 | 43 | 41 | 2 | 15 | 0.14
8 | 44 | 44 | 0 | 15 | 0.22
9 | 44 | 43 | 1 | 15 | 0.2
10 | 28 | 27 | 1 | 15 | 0.23
11 | 30 | 28 | 2 | 15 | 0.28
12 | 28 | 25 | 3 | 15 | 0.31
13 | 27 | 24 | 3 | 15 | 0.27
14 | 30 | 29 | 1 | 15 | 0.31
15 | 31 | 30 | 1 | 15 | 0.22
16 | 30 | 29 | 1 | 15 | 0.28
17 | 29 | 27 | 2 | 15 | 0.26
18 | 29 | 27 | 2 | 15 | 0.28
19 | 31 | 29 | 2 | 15 | 0.26
20 | 30 | 29 | 1 | 15 | 0.3
21 | 30 | 28 | 2 | 15 | 0.37
22 | 30 | 29 | 1 | 15 | 0.32
23 | 28 | 27 | 1 | 15 | 0.29
24 | 27 | 26 | 1 | 15 | 0.31
25 | 27 | 26 | 1 | 15 | 0.28
26 | 30 | 29 | 1 | 15 | 0.24
27 | 28 | 27 | 1 | 15 | 0.29
28 | 30 | 28 | 2 | 15 | 0.19
29 | 29 | 27 | 2 | 15 | 0.19
30 | 29 | 27 | 2 | 15 | 0.25
31 | 29 | 28 | 1 | 15 | 0.21
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 04/06/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2025-03-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 11 | 426 | y | 2360 | 0 | 0%
2 | 11 | 469 | y | 2546 | 0 | 0%
3 | 15 | 357 | y | 2430 | 0 | 0%
4 | 14.5 | 381 | y | 2274 | 0 | 0%
5 | 14 | 385 | y | 2324 | 0 | 0%
6 | 10.5 | 500 | y | 2837 | 0 | 0%
7 | 11 | 466 | y | 2820 | 0 | 0%
8 | 12 | 439 | y | 2468 | 0 | 0%
9 | 10.5 | 487 | y | 3254 | 0 | 0%
10 | 10.5 | 480 | y | 2520 | 0 | 0%
11 | 11 | 430 | y | 2208 | 0 | 0%
12 | 11.5 | 450 | y | 2617 | 0 | 0%
13 | 11 | 440 | y | 2679 | 0 | 0%
14 | 10.5 | 493 | y | 1828 | 0 | 0%
15 | 11.5 | 465 | y | 1450 | 0 | 0%
16 | 10.5 | 495 | y | 2501 | 0 | 0%
17 | 10 | 470 | y | 2650 | 0 | 0%
18 | 10 | 500 | y | 2220 | 0 | 0%
19 | 11 | 468 | y | 2037 | 0 | 0%
20 | 10 | 506 | y | 2060 | 0 | 0%
21 | 10.5 | 480 | y | 2200 | 0 | 0%
22 | 10.5 | 485 | y | 2054 | 0 | 0%
23 | 10 | 491 | y | 1924 | 0 | 0%
24 | 10.5 | 472 | y | 3170 | 0 | 0%
25 | 10.5 | 475 | y | 3186 | 0 | 0%
26 | 11 | 471 | y | 2489 | 0 | 0%
27 | 11 | 449 | y | 2696 | 0 | 0%
28 | 11 | 462 | y | 2136 | 0 | 0%
29 | 11 | 471 |  | 2022 | 0 | 0%
30 | 11 | 464 |  | 2576 | 0 | 0%
31 | 10.5 | 477 |  | 2711 | 0 | 0%
75247
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2025-04-06
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%