## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-04-24
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 28 | 26 | 2 | 15 | 0.39
2 | 31 | 29 | 2 | 15 | 0.24
3 | 26 | 25 | 1 | 15 | 0.27
4 | 27 | 26 | 1 | 15 | 0.26
5 | 28 | 25 | 3 | 15 | 0.32
6 | 28 | 27 | 1 | 15 | 0.27
7 | 36 | 28 | 8 | 15 | 0.29
8 | 34 | 32 | 2 | 15 | 0.38
9 | 30 | 28 | 2 | 15 | 0.35
10 | 36 | 34 | 2 | 15 | 0.29
11 | 41 | 42 | -1 | 15 | 0.19
12 | 30 | 30 | 0 | 15 | 0.14
13 | 30 | 30 | 0 | 15 | 0.29
14 | 45 | 44 | 1 | 15 | 0.31
15 | 31 | 29 | 2 | 15 | 0.25
16 | 29 | 27 | 2 | 15 | 0.28
17 | 29 | 27 | 2 | 15 | 0.24
18 | 29 | 28 | 1 | 15 | 0.31
19 | 27 | 26 | 1 | 15 | 0.23
20 | 29 | 28 | 1 | 15 | 0.2
21 | 29 | 28 | 1 | 15 | 0.19
22 | 31 | 29 | 2 | 15 | 0.31
23 | 31 | 29 | 2 | 15 | 0.22
24 | 31 | 29 | 2 | 15 | 0.2
25 | 31 | 29 | 2 | 15 | 0.16
26 | 30 | 29 | 1 | 15 | 0.19
27 | 29 | 28 | 1 | 15 | 0.17
28 | 31 | 29 | 2 | 15 | 0.16
29 | 30 | 28 | 2 | 15 | 0.19
30 | 29 | 27 | 2 | 15 | 0.17
31 |  |  |  | 15
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 05/01/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2025-04-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 12 | 423 | y | 1803 | 0 | 0%
2 | 11 | 460 | y | 2290 | 0 | 0%
3 | 10 | 488 | y | 2440 | 0 | 0%
4 | 14 | 372 | y | 1895 | 0 | 0%
5 | 10 | 483 | y | 2568 | 0 | 0%
6 | 14.5 | 378 | y | 3036 | 0 | 0%
7 | 10 | 470 | y | 2865 | 0 | 0%
8 | 10.5 | 460 | y | 2032 | 0 | 0%
9 | 10 | 470 | y | 2686 | 0 | 0%
10 | 10.5 | 465 | y | 2032 | 0 | 0%
11 | 10.5 | 455 | y | 2686 | 0 | 0%
12 | 11.5 | 428 | y | 2379 | 0 | 0%
13 | 11 | 430 | y | 2923 | 0 | 0%
14 | 13.5 | 408 | y | 2246 | 0 | 0%
15 | 11.5 | 436 | y | 3168 | 0 | 0%
16 | 10.5 | 448 | y | 2304 | 0 | 0%
17 | 10.5 | 438 | y | 2940 | 0 | 0%
18 | 10 | 468 | y | 2859 | 0 | 0%
19 | 10.5 | 436 | y | 3782 | 0 | 0%
20 | 10.5 | 438 | y | 6700 | 0 | 0%
21 | 10.5 | 435 | y | 4196 | 0 | 0%
22 | 11 | 438 | y | 4029 | 0 | 0%
23 | 11 | 441 | y | 4660 | 0 | 0%
24 | 11 | 435 | y | 3625 | 0 | 0%
25 | 11 | 417 | y | 3744 | 0 | 0%
26 | 10.5 | 433 | y | 5379 | 0 | 0%
27 | 11 | 419 | y | 3840 | 0 | 0%
28 | 11 | 422 | y | 3454 | 0 | 0%
29 | 10.5 | 424 |  | 4556 | 0 | 0%
30 | 10.5 | 414 |  | 5026 | 0 | 0%
31 |  |  |  |  | 0 | #DIV/0!
98143
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2025-05-01
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%