## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-05-25
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 29 | 27 | 2 | 15 | 0.17
2 | 30 | 28 | 2 | 15 | 0.15
3 | 42 | 40 | 2 | 15 | 0.14
4 | 30 | 28 | 2 | 15 | 0.13
5 | 30 | 29 | 1 | 15 | 0.12
6 | 30 | 28 | 2 | 15 | 0.4
7 | 30 | 28 | 2 | 15 | 0.16
8 | 31 | 28 | 3 | 15 | 0.19
9 | 32 | 26 | 6 | 15 | 0.33
10 | 30 | 26 | 4 | 15 | 0.24
11 | 30 | 28 | 2 | 15 | 0.21
12 | 28 | 27 | 1 | 15 | 0.18
13 | 30 | 28 | 2 | 15 | 0.24
14 | 29 | 21 | 8 | 15 | 0.21
15 | 30 | 27 | 3 | 15 | 0.26
16 | 30 | 28 | 2 | 15 | 0.43
17 | 29 | 27 | 2 | 15 | 0.31
18 | 29 | 27 | 2 | 15 | 0.29
19 | 30 | 28 | 2 | 15 | 0.21
20 | 30 | 28 | 2 | 15 | 0.17
21 | 30 | 28 | 2 | 15 | 0.18
22 | 30 | 28 | 2 | 15 | 0.18
23 | 30 | 28 | 2 | 15 | 0.22
24 | 30 | 28 | 2 | 15 | 0.19
25 | 31 | 29 | 2 | 15 | 0.24
26 | 30 | 28 | 2 | 15 | 0.26
27 | 28 | 26 | 2 | 15 | 0.27
28 | 31 | 29 | 2 | 15 | 0.15
29 | 30 | 28 | 2 | 15 | 0.18
30 | 30 | 28 | 2 | 15 | 0.26
31 | 31 | 29 | 2 | 15 | 0.19
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 06/01/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2025-05-01
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 10.5 | 416 |  | 4372 | 0 | 0%
2 | 11.5 | 397 | y | 4260 | 0 | 0%
3 | 11 | 392 | y | 5947 | 0 | 0%
4 | 11 | 398 | y | 7041 | 0 | 0%
5 | 11.5 | 387 | y | 6466 | 0 | 0%
6 | 11 | 400 | y | 4003 | 0 | 0%
7 | 11 | 387 | y | 5501 | 0 | 0%
8 | 10 | 405 | y | 6546 | 0 | 0%
9 | 10 | 390 | y | 5700 | 0 | 0%
10 | 10.5 | 374 | y | 4857 | 0 | 0%
11 | 10.5 | 370 | y | 4788 | 0 | 0%
12 | 10.5 | 385 | y | 5658 | 0 | 0%
13 | 11 | 365 | y | 3628 | 0 | 0%
14 | 11 | 360 | y | 5443 | 0 | 0%
15 | 11 | 370 | y | 6440 | 0 | 0%
16 | 11 | 444 | y | 7827 | 0 | 0%
17 | 10 | 453 | y | 6690 | 0 | 0%
18 | 11 | 422 | y | 4257 | 0 | 0%
19 | 10 | 449 | y | 4656 | 0 | 0%
20 | 11 | 426 | y | 3480 | 0 | 0%
21 | 11 | 425 | y | 4004 | 0 | 0%
22 | 11 | 415 | y | 4384 | 0 | 0%
23 | 11 | 430 | y | 1879 | 0 | 0%
24 | 11 | 436 | y | 5900 | 0 | 0%
25 | 11 | 423 | y | 5861 | 0 | 0%
26 | 10.5 | 406 | y | 4699 | 0 | 0%
27 | 11 | 414 | y | 6333 | 0 | 0%
28 | 11 | 425 | y | 5114 | 0 | 0%
29 | 11 | 410 |  | 5760 | 0 | 0%
30 | 11 | 417 |  | 5337 | 0 | 0%
31 | 11 | 415 |  | 7272 | 0 | 0%
164103
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2025-06-01
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%