## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-06-25
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 39 | 1 | 15 | 0.26
2 | 41 | 40 | 1 | 15 | 0.18
3 | 30 | 28 | 2 | 15 | 0.29
4 | 30 | 28 | 2 | 15 | 0.25
5 | 30 | 27 | 3 | 15 | 0.15
6 | 30 | 28 | 2 | 15 | 0.17
7 | 34 | 36 | -2 | 15 | 0.22
8 | 30 | 28 | 2 | 15 | 0.14
9 | 31 | 28 | 3 | 15 | 0.16
10 | 29 | 26 | 3 | 15 | 0.15
11 | 29 | 27 | 2 | 15 | 0.29
12 | 29 | 27 | 2 | 15 | 0.3
13 | 31 | 28 | 3 | 15 | 0.16
14 | 30 | 28 | 2 | 15 | 0.19
15 | 30 | 27 | 3 | 15 | 0.2
16 | 30 | 28 | 2 | 15 | 0.19
17 | 30 | 28 | 2 | 15 | 0.23
18 | 30 | 27 | 3 | 15 | 0.24
19 | 30 | 28 | 2 | 15 | 0.12
20 | 43 | 42 | 1 | 15 | 0.13
21 | 38 | 36 | 2 | 15 | 0.2
22 | 30 | 28 | 2 | 15 | 0.14
23 | 30 | 28 | 2 | 15 | 0.13
24 | 30 | 27 | 3 | 15 | 0.16
25 | 30 | 27 | 3 | 15 | 0.14
26 | 30 | 27 | 3 | 15 | 0.17
27 | 31 | 29 | 2 | 15 | 0.18
28 | 30 | 28 | 2 | 15 | 0.21
29 | 31 | 28 | 3 | 15 | 0.22
30 | 30 | 28 | 2 | 15 | 0.2
31 |  |  |  | 15
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 07/03/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2025-07-03
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 10.5 | 419 | y | 6550 | 0 | 0%
2 | 11 | 407 | y | 5980 | 0 | 0%
3 | 11.5 | 392 | y | 5716 | 0 | 0%
4 | 11 | 400 | y | 6440 | 0 | 0%
5 | 10.5 | 398 | y | 7606 | 0 | 0%
6 | 11 | 379 | y | 6391 | 0 | 0%
7 | 11 | 375 | y | 5258 | 0 | 0%
8 | 11.5 | 377 | y | 5422 | 0 | 0%
9 | 11.5 | 370 | y | 7035 | 0 | 0%
10 | 12.5 | 320 | y | 8336 | 0 | 0%
11 | 10.5 | 310 | y | 7350 | 0 | 0%
12 | 11 | 355 | y | 7128 | 0 | 0%
13 | 11 | 375 | y | 6512 | 0 | 0%
14 | 12 | 342 | y | 5923 | 0 | 0%
15 | 11 | 354 | y | 5645 | 0 | 0%
16 | 11 | 366 | y | 9528 | 0 | 0%
17 | 10.5 | 355 | y | 7220 | 0 | 0%
18 | 10.5 | 351 | y | 6064 | 0 | 0%
19 | 11.5 | 340 | y | 6034 | 0 | 0%
20 | 11 | 325 | y | 6160 | 0 | 0%
21 | 11.5 | 342 | y | 3600 | 0 | 0%
22 | 11 | 341 | y | 4613 | 0 | 0%
23 | 11.5 | 309 | y | 2414 | 0 | 0%
24 | 11.5 | 312 | y | 3539 | 0 | 0%
25 | 11 | 428 | y | 6875 | 0 | 0%
26 | 11.5 | 445 | y | 8377 | 0 | 0%
27 | 11.5 | 443 | y | 4627 | 0 | 0%
28 | 11.5 | 448 | y | 4920 | 0 | 0%
29 | 11.5 | 410 | y | 7659 | 0 | 0%
30 | 11 | 417 | y | 7420 | 0 | 0%
31 |  |  |  |  | 0 | #DIV/0!
186342
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2025-06-01
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%