## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-07-25
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 31 | 28 | 3 | 15 | 0.13
2 | 30 | 27 | 3 | 15 | 0.12
3 | 30 | 28 | 2 | 15 | 0.11
4 | 30 | 27 | 3 | 15 | 0.13
5 | 42 | 40 | 2 | 15 | 0.14
6 | 44 | 43 | 1 | 15 | 0.14
7 | 36 | 33 | 3 | 15 | 0.24
8 | 41 | 39 | 2 | 15 | 0.1
9 | 30 | 28 | 2 | 15 | 0.09
10 | 29 | 26 | 3 | 15 | 0.14
11 | 30 | 28 | 2 | 15 | 0.14
12 | 28 | 26 | 2 | 15 | 0.24
13 | 30 | 27 | 3 | 15 | 0.16
14 | 31 | 28 | 3 | 15 | 0.16
15 | 31 | 28 | 3 | 15 | 0.14
16 | 31 | 28 | 3 | 15 | 0.14
17 | 29 | 26 | 3 | 15 | 0.17
18 | 29 | 26 | 3 | 15 | 0.14
19 | 31 | 28 | 3 | 15 | 0.29
20 | 31 | 28 | 3 | 15 | 0.26
21 | 30 | 27 | 3 | 15 | 0.21
22 | 30 | 28 | 2 | 15 | 0.23
23 | 30 | 28 | 2 | 15 | 0.12
24 | 31 | 28 | 3 | 15 | 0.13
25 | 31 | 28 | 3 | 15 | 0.16
26 | 30 | 27 | 3 | 15 | 0.19
27 | 31 | 29 | 2 | 15 | 0.15
28 | 34 | 30 | 4 | 15 | 0.18
29 | 37 | 32 | 5 | 15 | 0.16
30 | 40 | 35 | 5 | 15 | 0.2
31 | 42 | 36 | 6 | 15 | 0.2
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 08/03/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2025-07-03
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 11.5 | 443 | y | 7304 | 0 | 0%
2 | 11.5 | 442 | y | 7086 | 0 | 0%
3 | 11 | 439 | y | 6777 | 0 | 0%
4 | 11 | 430454 | y | 7020 | 0 | 0%
5 | 10.5 | 417 | y | 6969 | 0 | 0%
6 | 11.5 | 412 | y | 7819 | 0 | 0%
7 | 11.5 | 415 | y | 9830 | 0 | 0%
8 | 11.5 | 397 | y | 7920 | 0 | 0%
9 | 11.5 | 388 | y | 7620 | 0 | 0%
10 | 12 | 396 | y | 11190 | 0 | 0%
11 | 11.5 | 380 | y | 8360 | 0 | 0%
12 | 10.5 | 380 | y | 7165 | 0 | 0%
13 | 10.5 | 372 | y | 7152 | 0 | 0%
14 | 11.5 | 361 | y | 9074 | 0 | 0%
15 | 11.5 | 362 | y | 7367 | 0 | 0%
16 | 11.5 | 353 | y | 10204 | 0 | 0%
17 | 11 | 339 | y | 10979 | 0 | 0%
18 | 11 | 354 | y | 8904 | 0 | 0%
19 | 11 | 352 | y | 5773 | 0 | 0%
20 | 11.5 | 355 | y | 7896 | 0 | 0%
21 | 11 | 344 | y | 8750 | 0 | 0%
22 | 11 | 329 | y | 5740 | 0 | 0%
23 | 11 | 344 | y | 7614 | 0 | 0%
24 | 11.5 | 329 | y | 7049 | 0 | 0%
25 | 11.5 | 325 | y | 7622 | 0 | 0%
26 | 11.5 | 315 | y | 6987 | 0 | 0%
27 | 11.5 | 316 | y | 6267 | 0 | 0%
28 | 10.5 | 340 | y | 7670 | 0 | 0%
29 | 12 | 309 | y | 5353 | 0 | 0%
30 | 11.5 | 308 | y | 9868 | 0 | 0%
31 | 12 | 299 | y | 7544 | 0 | 0%
242873
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2025-08-01
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%