## Turbidity
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-25
System Name: | Country Club Estates WD |  |  | PWS ID#: | 41-01501 | WTP ID: | TP FOR CBNB
Day | 41 | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 46 | 44 | 2 | 15 | 0.13
2 | 45 | 38 | 7 | 15 | 0.1
3 | 45 | 44 | 1 | 15 | 0.1
4 | 31 | 26 | 5 | 15 | 0.11
5 | 30 | 25 | 5 | 15 | 0.17
6 | 30 | 26 | 4 | 15 | 0.14
7 | 29 | 25 | 4 | 15 | 0.16
8 | 31 | 26 | 5 | 15 | 0.18
9 | 31 | 26 | 5 | 15 | 0.17
10 | 33 | 28 | 5 | 15 | 0.19
11 | 33 | 28 | 5 | 15 | 0.25
12 | 30 | 26 | 4 | 15 | 0.14
13 | 33 | 28 | 5 | 15 | 0.16
14 | 34 | 28 | 6 | 15 | 0.15
15 | 32 | 26 | 6 | 15 | 0.14
16 | 29 | 25 | 4 | 15 | 0.24
17 | 36 | 30 | 6 | 15 | 0.34
18 | 32 | 27 | 5 | 15 | 0.34
19 | 32 | 26 | 6 | 15 | 0.21
20 | 35 | 29 | 6 | 15 | 0.26
21 | 35 | 30 | 5 | 15 | 0.25
22 | 35 | 30 | 5 | 15 | 0.21
23 | 36 | 30 | 6 | 15 | 0.17
24 | 35 | 30 | 5 | 15 | 0.2
25 | 35 | 30 | 5 | 15 | 0.12
26 | 35 | 30 | 5 | 15 | 0.13
27 | 35 | 30 | 5 | 15 | 0.25
28 | 32 | 26 | 6 | 15 | 0.14
29 | 36 | 30 | 6 | 15 | 0.14
30 | 36 | 30 | 6 | 15 | 0.15
31 | 32 | 26 | 6 | 15 | 0.2
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary UV Summary (Circle Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | Is any off -spec water produced in the month
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: | Mark Merry
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 09/02/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: 503-812-7320 |  | CERT #: T-5204
1 Including continuous NTU data, if applicable, for optimization recording purposes.
No

## UV
Oregon DHS - Drinking Water Services – Surface Water Quality Data
System Name: |  | Country Club Estates WD |  | ID# 41 | 1501 | Month/Year: | 2025-08-03
Minimum Validated UVT : |  |  | 75% |  |  | Duty sensor variation from reference sensor %: | 1.0 % 0%
Date | Peak Hourly Demand Flow | Minimum | All Lamps On? | Daily Water Produced {A} | Water outside Validated Conditions {B} | Cumulative % Off-Spec Water Produced
Dose
| [gpm/unit] | [mJ/cm2] | [ Y or N ] | [gal] | [gal] | (Mo. Sum {B}) ¸ (Mo. Sum {A}) * 100
[%]
1 | 10.5 | 337 | y | 7330 | 0 | 0%
2 | 11 | 290 | y | 6912 | 0 | 0%
3 | 11.5 | 442 | y | 7502 | 0 | 0%
4 | 11 | 472 | y | 6977 | 0 | 0%
5 | 10.5 | 444 | y | 5469 | 0 | 0%
6 | 10.5 | 441 | y | 6380 | 0 | 0%
7 | 10.5 | 446 | y | 11510 | 0 | 0%
8 | 10.5 | 441 | y | 8263 | 0 | 0%
9 | 10.5 | 429 | y | 6593 | 0 | 0%
10 | 11.5 | 416 | y | 6980 | 0 | 0%
11 | 11.5 | 419 | y | 8588 | 0 | 0%
12 | 10.5 | 412 | y | 7669 | 0 | 0%
13 | 11.5 | 400 | y | 8202 | 0 | 0%
14 | 11.5 | 450 | y | 8900 | 0 | 0%
15 | 11.5 | 396 | y | 8040 | 0 | 0%
16 | 10.5 | 489 | y | 3328 | 0 | 0%
17 | 10.5 | 485 | y | 10560 | 0 | 0%
18 | 10 | 478 | y | 8344 | 0 | 0%
19 | 10.5 | 485 | y | 5845 | 0 | 0%
20 | 10.5 | 465 | y | 5847 | 0 | 0%
21 | 11 | 429 | y | 6321 | 0 | 0%
22 | 10.5 | 450 | y | 6120 | 0 | 0%
23 | 11 | 430 | y | 7785 | 0 | 0%
24 | 11 | 433 | y | 5164 | 0 | 0%
25 | 11.5 | 409 | y | 9870 | 0 | 0%
26 | 11 | 407 | y | 6553 | 0 | 0%
27 | 10 | 420 | y | 12009 | 0 | 0%
28 | 10 | 409 | y | 12152 | 0 | 0%
29 | 11.5 | 376 | y | 11127 | 0 | 0%
30 | 11 | 389 | y | 16883 | 0 | 0%
31 | 11 | 385 | y | 7618 | 0 | 0%
250841
rev 1/11 I:\MC\forms\Turbidity Report Form – UV and opt mod.doc
Signature: |  | Mark Merry |  | Op Cert #: | T-5204 | Date: | 2025-09-02
Note on G7: Downs Munoz Kent Orvill: water that made it into the storage tanks and/or into distribution before UV reactor was able to provide a minimum of 186 mJ/cm2, or water that for other reasons bypassed UV reactor and went to storage/distribution without meeting minimum dose ( 186 mJ/cm2).
Note on I5: Downs Munoz Kent Orvill: Should not be above or below 20%