## Sheet1
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Lane
Cartridge or Bag Filtration | [5 empty] | Month/Year: | August 2025
System Name: | Fern Acres |  |  | ID#: 41 | 01563 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 2 | 18 | 45 | 0.15 | 0.15
2 | 20 | 2 | 18 | 45 | 0.13 | 0.13
3 | 20 | 2 | 18 | 45 | 0.15 | 0.15
4 | 20 | 2 | 18 | 45 | 0.13 | 0.13
5 | 20 | 2 | 18 | 45 | 0.15 | 0.15
6 | 20 | 2 | 18 | 45 | 0.13 | 0.13
7 | 20 | 2 | 18 | 45 | 0.13 | 0.13
8 | 28 | 2 | 26 | 45 | 0.18 | 0.18
9 | 28 | 2 | 26 | 45 | 0.18 | 0.18
10 | 24 | 2 | 22 | 45 | 0.21 | 0.21
11 | 20 | 2 | 18 | 45 | 0.54 | 0.54
12 | 29 | 2 | 27 | 45 | 0.19 | 0.19
13 | 24 | 2 | 22 | 45 | 0.19 | 0.19
14 | 22 | 2 | 20 | 45 | 0.16 | 0.16
15 | 20 | 2 | 18 | 45 | 0.2 | 0.2
16 | 20 | 2 | 18 | 45 | 0.2 | 0.2
17 | 20 | 2 | 18 | 45 | 0.18 | 0.18
18 | 20 | 2 | 18 | 45 | 0.21 | 0.21
19 | 20 | 2 | 18 | 45 | 0.2 | 0.2
20 | 21 | 2 | 19 | 45 | 0.18 | 0.18
21 | 21 | 2 | 19 | 45 | 0.19 | 0.19
22 | 21 | 2 | 19 | 45 | 0.18 | 0.18
23 | 21 | 2 | 19 | 45 | 0.19 | 0.19
24 | 21 | 2 | 19 | 45 | 0.19 | 0.19
25 | 20 | 2 | 18 | 45 | 0.18 | 0.18
26 | 20 | 2 | 18 | 45 | 0.21 | 0.21
27 | 20 | 2 | 18 | 45 | 0.18 | 0.18
28 | 20 | 2 | 18 | 45 | 0.17 | 0.17
29 | 20 | 2 | 18 | 45 | 0.2 | 0.2
30 | 20 | 2 | 18 | 45 | 0.2 | 0.2
31 | 20 | 2 | 18 | 45 | 0.19 | 0.19
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Dan Reitz
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 2025-09-08
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541) 342-1718 |  | CERT #: 6528
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Fern Acres |  | ID#: 41 | 01563 | Month/Year: | August 2025 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.63 | 130 | 81.9 | 18.4 | 7.69 | 26.8758 | YES | 18
2 | 0.66 | 130 | 85.8 | 18.6 | 7.69 | 26.6093 | YES | 18
3 | 0.61 | 130 | 79.3 | 18.3 | 7.52 | 25.3391 | YES | 18
4 | 0.69 | 130 | 89.7 | 18 | 7.71 | 28.0024 | YES | 18
5 | 0.64 | 130 | 83.2 | 19.6 | 7.62 | 24.1865 | YES | 18
6 | 0.63 | 130 | 81.9 | 19.3 | 7.54 | 23.9255 | YES | 18
7 | 0.66 | 130 | 85.8 | 18.9 | 7.62 | 25.4085 | YES | 18
8 | 0.67 | 130 | 87.1 | 19.7 | 7.69 | 24.7452 | YES | 18
9 | 0.62 | 130 | 80.6 | 19.4 | 7.48 | 23.2118 | YES | 18
10 | 0.7 | 130 | 91 | 21.3 | 7.72 | 22.5489 | YES | 18
11 | 0.67 | 130 | 87.1 | 20.5 | 7.61 | 22.7592 | YES | 18
12 | 0.8 | 130 | 104 | 19.7 | 7.6 | 24.2877 | YES | 18
13 | 0.68 | 130 | 88.4 | 20.1 | 7.63 | 23.5825 | YES | 18
14 | 0.62 | 130 | 80.6 | 20.3 | 7.55 | 22.4265 | YES | 18
15 | 1.15 | 130 | 149.5 | 19.1 | 7.54 | 25.7386 | YES | 18
16 | 0.83 | 130 | 107.9 | 20 | 7.7 | 24.793 | YES | 18
17 | 0.71 | 130 | 92.3 | 20.5 | 7.58 | 22.609 | YES | 18
18 | 0.69 | 130 | 89.7 | 19.2 | 7.62 | 24.9879 | YES | 18
19 | 0.7 | 130 | 91 | 18.5 | 7.7 | 27.0112 | YES | 18
20 | 0.52 | 130 | 67.6 | 18.8 | 7.64 | 25.3608 | YES | 18
21 | 0.54 | 130 | 70.2 | 19.3 | 7.65 | 24.6719 | YES | 18
22 | 0.57 | 130 | 74.1 | 17.6 | 7.64 | 27.6419 | YES | 18
23 | 0.53 | 130 | 68.9 | 18.1 | 7.59 | 26.1192 | YES | 18
24 | 0.52 | 130 | 67.6 | 18.1 | 7.63 | 26.4807 | YES | 18
25 | 0.45 | 130 | 58.5 | 18.5 | 7.54 | 24.7306 | YES | 18
26 | 0.55 | 130 | 71.5 | 19.5 | 7.55 | 23.4776 | YES | 18
27 | 0.59 | 130 | 76.7 | 18.8 | 7.62 | 25.3752 | YES | 18
28 | 0.6 | 130 | 78 | 17.9 | 7.71 | 27.902 | YES | 18
29 | 0.57 | 130 | 74.1 | 18.5 | 7.7 | 26.6126 | YES | 18
30 | 0.54 | 130 | 70.2 | 18.1 | 7.63 | 26.5413 | YES | 18
31 | 0.51 | 130 | 66.3 | 18.4 | 7.54 | 25.069 | YES | 18
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2