## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | TILLAMOOK
Conventional or Direct Filtration | [6 empty] | Month/Year: | April 2024
| Brighton Water Co |  |  | ID#: 41 | 05104 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  | 0.38
2 |  |  |  | 0.38
3 |  |  |  | 0.38
4 |  |  |  | 0.35
5 |  |  |  | 0.35
6 |  |  |  | 0.35
7 |  |  |  | 0.32
8 |  |  |  | 0.32
9 |  |  |  | 0.35
10 |  |  |  | 0.38
11 |  |  |  | 0.35
12 |  |  |  | 0.32
13 |  |  |  | 0.32
14 |  |  |  | 0.32
15 |  |  |  | 0.3
16 |  |  |  | 0.3
17 |  |  |  | 0.3
18 |  |  |  | 0.32
19 |  |  |  | 0.32
20 |  |  |  | 0.35
21 |  |  |  | 0.35
22 |  |  |  | 0.38
23 |  |  |  | 0.4
24 |  |  |  | 0.38
25 |  |  |  | 0.35
26 |  |  |  | 0.4
27 |  |  |  | 0.42
28 |  |  |  | 0.45
29 |  |  |  | 0.5
30 |  |  |  | 0.5
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  |  | yes |  | yes
All turbidity readings < IFE2 triggers |  |  |  | yes
Sherri Stewart
SIGNATURE:
[5 empty] | 503-647-6485 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Brighton Water Co |  | ID#: 41 | 05104 |  |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.21 |  | 0 |  |  | 8.4798 | yes
2 | 0.21 |  | 0 |  |  | 8.4798 | yes
3 | 0.21 |  | 0 |  |  | 8.4798 | yes
4 | 0.21 |  | 0 |  |  | 8.4798 | yes
5 | 0.2 |  | 0 |  |  | 8.4745 | yes
6 | 0.2 |  | 0 |  |  | 8.4745 | yes
7 | 0.2 |  | 0 |  |  | 8.4745 | yes
8 | 0.21 |  | 0 |  |  | 8.4798 | yes
9 | 0.21 |  | 0 |  |  | 8.4798 | yes
10 | 0.2 |  | 0 |  |  | 8.4745 | yes
11 | 0.2 |  | 0 |  |  | 8.4745 | yes
12 | 0.2 |  | 0 |  |  | 8.4745 | yes
13 | 0.21 |  | 0 |  |  | 8.4798 | yes
14 | 0.21 |  | 0 |  |  | 8.4798 | yes
15 | 0.21 |  | 0 |  |  | 8.4798 | yes
16 | 0.21 |  | 0 |  |  | 8.4798 | yes
17 | 0.2 |  | 0 |  |  | 8.4745 | yes
18 | 0.2 |  | 0 |  |  | 8.4745 | yes
19 | 0.2 |  | 0 |  |  | 8.4745 | yes
20 | 0.2 |  | 0 |  |  | 8.4745 | yes
21 | 0.2 |  | 0 |  |  | 8.4745 | yes
22 | 0.2 |  | 0 |  |  | 8.4745 | yes
23 | 0.21 |  | 0 |  |  | 8.4798 | yes
24 | 0.21 |  | 0 |  |  | 8.4798 | yes
25 | 0.2 |  | 0 |  |  | 8.4745 | yes
26 | 0.2 |  | 0 |  |  | 8.4745 | yes
27 | 0.2 |  | 0 |  |  | 8.4745 | yes
28 | 0.21 |  | 0 |  |  | 8.4798 | yes
29 | 0.21 |  | 0 |  |  | 8.4798 | yes
30 | 0.21 |  | 0 |  |  | 8.4798 | yes
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2
Note on D49: ok per Gregg