## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Coos
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2020-01-01
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  |  | WTP : TP - | A
Day | 24:00 [NTU] | 04:00 [NTU] | 08:00 [NTU] | 12:00 [NTU] | 16:00 [NTU] | 20:00 [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  |  | 0.54 |  | 0.54
2 |  |  |  | 0.02 |  |  | 0.021
3 |  |  |  |  | 0.02 |  | 0.02
4 |  |  |  |  | 0.027 |  | 0.027
5 |  |  |  |  | 0.036 |  | 0.036
6 |  |  |  |  | 0.039 |  | 0.039
7 |  |  |  |  | 0.038 |  | 0.038
8 |  |  |  |  | 0.034 |  | 0.034
9 |  |  |  |  | 0.044 |  | 0.044
10 |  |  |  |  | 0.019 |  | 0.019
11 |  |  |  |  | 0.028 |  | 0.028
12 |  |  |  |  | 0.035 |  | 0.035
13 |  |  |  |  | 0.019 |  | 0.019
14 |  |  |  |  | 0.019 |  | 0.019
15 |  |  |  |  | 0.022 |  | 0.022
16 |  |  |  |  | 0.023 |  | 0.023
17 |  |  |  |  | 0.019 |  | 0.019
18 |  |  |  |  | 0.019 |  | 0.019
19 |  |  |  |  | 0.019 |  | 0.019
20 |  |  |  |  | 0.019 |  | 0.019
21 |  |  |  |  | 0.02 |  | 0.02
22 |  |  |  |  | 0.019 |  | 0.019
23 |  |  |  |  | 0.021 |  | 0.021
24 |  |  |  |  | 0.029 |  | 0.029
25 |  |  |  |  | 0.02 |  | 0.02
26 |  |  |  |  | 0.029 |  | 0.029
27 |  |  |  |  | 0.029 |  | 0.029
28 |  |  |  |  | 0.026 |  | 0.026
29 |  |  |  |  | 0.025 |  | 0.025
30 |  |  |  |  | 0.02 |  | 0.02
31 |  |  |  |  | 0.029 |  | 0.029
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:02/10/2021
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #:T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Weiss Estates Water District |  | ID#: 41-05581 |  | Month/Year: | 2021-01-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—1700 | 0.26 | 75 | 19.5 | 10 | 7 | 17.7784 | YES | 12
2—1445 | 0.24 | 75 | 18 | 10 | 7 | 17.7393 | YES | 12
3—1510 | 0.36 | 75 | 27 | 10 | 7 | 17.9753 | YES | 12
4 | 0.34 | 75 | 25.5 | 10 | 7 | 17.9357 | YES | 12
5 | 0.28 | 75 | 21 | 10 | 7.1 | 18.4403 | YES | 12
6 | 0.28 | 75 | 21 | 10 | 7 | 17.8176 | YES | 12
7 | 0.42 | 75 | 31.5 | 10 | 7 | 18.0947 | YES | 12
8 | 0.64 | 75 | 48 | 10 | 7.1 | 19.1915 | YES | 12
9 | 0.63 | 75 | 47.25 | 10 | 7 | 18.5196 | YES | 12
10 | 0.92 | 75 | 69 | 10 | 7 | 19.125 | YES | 12
11 | 0.81 | 75 | 60.75 | 10 | 7 | 18.8928 | YES | 12
12 | 0.9 | 75 | 67.5 | 10 | 7 | 19.0826 | YES | 12
13 | 0.84 | 75 | 63 | 10 | 7 | 18.9558 | YES | 12
14 | 0.64 | 75 | 48 | 10 | 7 | 18.5401 | YES | 12
15 | 0.3 | 75 | 22.5 | 12 | 6.9 | 15.2001 | YES | 12
16 | 0.25 | 75 | 18.75 | 12 | 6.9 | 15.1186 | YES | 12
17 | 0.4 | 75 | 30 | 12 | 6.9 | 15.3647 | YES | 12
18—1415 | 0.62 | 75 | 46.5 | 12 | 6.9 | 15.734 | YES | 12
19—1445 | 0.85 | 75 | 63.75 | 11 | 7 | 17.7901 | YES | 12
20—1140 | 0.78 | 75 | 58.5 | 11 | 7.1 | 18.2698 | YES | 12
21—1405 | 0.58 | 75 | 43.5 | 11 | 7 | 17.27 | YES | 12
22—1510 | 0.64 | 75 | 48 | 11 | 6.9 | 16.8017 | YES | 12
23—1030 | 0.57 | 75 | 42.75 | 10 | 7 | 18.3971 | YES | 12
24—1030 | 0.5 | 75 | 37.5 | 10 | 7 | 18.2553 | YES | 12
25—1400 | 0.54 | 75 | 40.5 | 9 | 7 | 19.5643 | YES | 12
26—1600 | 0.37 | 75 | 27.75 | 9 | 7.6 | 23.6872 | YES | 12
27—1530 | 0.65 | 75 | 48.75 | 9 | 7.3 | 21.9951 | YES | 12
28—1445 | 0.37 | 75 | 27.75 | 9 | 7.3 | 21.3115 | YES | 12
29—1615 | 0.7 | 75 | 52.5 | 9 | 7.2 | 21.3566 | YES | 12
30—1630 | 0.4 | 75 | 30 | 9 | 7.1 | 19.9416 | YES | 12
31 | 0.4 | 75 | 30 | 10 | 7 | 18.0548 | YES | 12
Revised October 2016-8 PAX
PAGE 2 of 2