## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | August 2021
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 26 | 26 | 0 | 5 | 0.122 | 0.122
2 | 27 | 27 | 0 | 5 | 0.171 | 0.171
3 | 29 | 28 | 1 | 5 | 0.166 | 0.166
4 | 4 | 4 | 0 | 5 | 0.119 | 0.119
5 | 4 | 4 | 0 | 5 | 0.481 | 0.481
6 | 4 | 4 | 0 | 5 | 0.109 | 0.109
7 | 24 | 23 | 1 | 5 | 0.295 | 0.295
8 | 27 | 26 | 1 | 5 | 0.104 | 0.104
9 | 29 | 29 | 0 | 5 | 0.466 | 0.466
10 | 28 | 27 | 1 | 5 | 0.332 | 0.332
11 | 28 | 28 | 0 | 5 | 0.314 | 0.314
12 | 28 | 27 | 1 | 5 | 0.365 | 0.365
13 | 27 | 27 | 0 | 5 | 0.338 | 0.338
14 | 4 | 4 | 0 | 5 | 0.362 | 0.362
15 | 4 | 4 | 0 | 5 | 0.332 | 0.332
16 | 3 | 3 | 0 | 5 | 0.287 | 0.287
17 | 27 | 26 | 1 | 5 | 0.355 | 0.355
18 | 28 | 27 | 1 | 5 | 0.485 | 0.485
19 | 3 | 3 | 0 | 5 | 0.495 | 0.495
20 | 27 | 27 | 0 | 5 | 0.327 | 0.327
21 | 26 | 26 | 0 | 5 | 0.415 | 0.415
22 | 27 | 26 | 1 | 5 | 0.501 | 0.501
23 | 3 | 3 | 0 | 5 | 0.438 | 0.438
24 | 26 | 25 | 1 | 5 | 0.548 | 0.548
25 | 27 | 26 | 1 | 5 | 0.724 | 0.724
26 | 27 | 26 | 1 | 5 | 0.593 | 0.593
27 | 3 | 3 | 0 | 5 | ..614 | 0.614
28 | 3 | 3 | 0 | 5 | 0.633 | 0.633
29 | 28 | 26 | 2 | 5 | 0.752 | 0.752
30 | 23 | 23 | 0 | 5 | 0.861 | 0.861
31 | 4 | 4 | 0 | 5 | 1.171 | 1.171
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 09/06/2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | August 2021 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.5 | 75 | 112.5 | 14 | 6.7 | 27.5819 | YES | 12
2—1545 | 0.94 | 75 | 70.5 | 18 | 6.5 | 18.3273 | YES | 12
3—1600 | 0.74 | 75 | 55.5 | 19 | 6.4 | 16.1066 | YES | 12
4—1530 | 0.6 | 75 | 45 | 19 | 6.5 | 16.4581 | YES | 12
5—1545 | 0.63 | 75 | 47.25 | 19 | 6.5 | 16.5157 | YES | 12
6—1630 | 0.57 | 75 | 42.75 | 19 | 6.7 | 17.6897 | YES | 12
7—1615 | 0.66 | 75 | 49.5 | 20 | 6.6 | 16.0782 | YES | 12
8—1545 | 0.77 | 75 | 57.75 | 20 | 6.6 | 16.2857 | YES | 12
9 | 0.97 | 75 | 72.75 | 20 | 6.7 | 17.3124 | YES | 12
10 | 0.82 | 75 | 61.5 | 20 | 6.7 | 17.0131 | YES | 12
11 | 0.91 | 75 | 68.25 | 20 | 6.7 | 17.1921 | YES | 12
12 | 0.98 | 75 | 73.5 | 22 | 6.6 | 14.5551 | YES | 12
13 | 0.75 | 75 | 56.25 | 20 | 6.6 | 16.2478 | YES | 12
14 | 0.59 | 75 | 44.25 | 18 | 6.6 | 18.2747 | YES | 12
15 | 0.52 | 75 | 39 | 20 | 6.7 | 16.4291 | YES | 12
16 | 0.43 | 75 | 32.25 | 20 | 6.6 | 15.6523 | YES | 12
17 | 0.31 | 75 | 23.25 | 20 | 6.6 | 15.4344 | YES | 12
18 | 0.43 | 75 | 32.25 | 20 | 6.6 | 15.6523 | YES | 12
19 | 0.31 | 75 | 23.25 | 18 | 6.6 | 17.6905 | YES | 12
20 | 0.29 | 75 | 21.75 | 20 | 6.7 | 15.9944 | YES | 12
21 | 0.27 | 75 | 20.25 | 20 | 6.7 | 15.9572 | YES | 12
22 | 0.48 | 75 | 36 | 20 | 6.6 | 15.744 | YES | 12
23 | 0.61 | 75 | 45.75 | 20 | 6.6 | 15.9847 | YES | 12
24 | 0.87 | 75 | 65.25 | 20 | 6.6 | 16.4766 | YES | 12
25 | 0.82 | 75 | 61.5 | 20 | 6.6 | 16.3809 | YES | 12
26 | 0.53 | 75 | 39.75 | 20 | 6.6 | 15.8362 | YES | 12
27 | 0.51 | 75 | 38.25 | 20 | 6.5 | 15.2101 | YES | 12
28 | 0.46 | 75 | 34.5 | 20 | 6.5 | 15.1214 | YES | 12
29 | 0.45 | 75 | 33.75 | 20 | 6.5 | 15.1037 | YES | 12
30—1420 | 0.62 | 75 | 46.5 | 20 | 6.7 | 16.6216 | YES | 12
31—1410 | 0.55 | 75 | 41.25 | 20 | 6.6 | 15.8732 | YES | 12
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2