## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | May 2022
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 20 | 0 | 5 | 0.014 | 0.014
2 | 20 | 20 | 0 | 5 | 0.023 | 0.023
3 | 20 | 20 | 0 | 5 | 0.083 | 0.083
4 | 18 | 18 | 0 | 5 | 0.019 | 0.019
5 | 17 | 17 | 0 | 5 | 0.054 | 0.054
6 | 16 | 15 | 1 | 5 | 0.014 | 0.014
7 | 21 | 20 | 1 | 5 | 0.035 | 0.035
8 | 0 | 0 | 0 | 5 | 0.067 | 0.067
9 | 0 | 0 | 0 | 5 | 0.052 | 0.052
10 | 21 | 20 | 1 | 5 | 0.082 | 0.082
11 | 22 | 22 | 0 | 5 | 0.069 | 0.069
12 | 0 | 0 | 0 | 5 | 0.057 | 0.057
13 | 0 | 0 | 0 | 5 | 0.071 | 0.071
14 | 19 | 19 | 0 | 5 | 0.059 | 0.059
15 | 0 | 0 | 0 | 5 | 0.072 | 0.072
16 | 0 | 0 | 0 | 5 | 0.014 | 0.014
17 | 0 | 0 | 0 | 5 | 0.0489 | 0.048
18 | 20 | 20 | 0 | 5 | 0.017 | 0.017
19 | 0 | 0 | 0 | 5 | 0.016 | 0.016
20 | 0 | 0 | 0 | 5 | 0.015 | 0.015
21 | 17 | 17 | 0 | 5 | 0.015 | 0.015
22 | 20 | 20 | 0 | 5 | 0.019 | 0.019
23 | 15 | 15 | 0 | 5 | 0.019 | 0.019
24 | 12 | 12 | 0 | 5 | 0.017 | 0.017
25 | 0 | 0 | 0 | 5 | 0.019 | 0.019
26 | 12 | 12 | 0 | 5 | 0.021 | 0.021
27 | 12 | 12 | 0 | 5 | 0.017 | 0.017
28 | 12 | 12 | 0 | 5 | 0.017 | 0.017
29 | 0 | 0 | 0 | 5 | 0.015 | 0.015
30 | 0 | 0 | 0 | 5 | 0.015 | 0.015
31 | 0 | 0 | 0 | 5 | 0.016 | 0.016
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 06/09/2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
All daily turbidity readings ≤ 5 NTU?
May | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | May 2022 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.83 | 75 | 137.25 | 14 | 7.5 | 38.5045 | YES | 12
2 | 1.52 | 75 | 114 | 14 | 7.3 | 34.5283 | YES | 12
3 | 1.89 | 75 | 141.75 | 14 | 7.4 | 37.3638 | YES | 12
4 | 0.55 | 75 | 41.25 | 14 | 7.2 | 29.7952 | YES | 12
5 | 0.45 | 75 | 33.75 | 14 | 7.3 | 30.5701 | YES | 12
6 | 0.73 | 75 | 54.75 | 12 | 7.1 | 34.0785 | YES | 12
7 | 0.58 | 75 | 43.5 | 14 | 7 | 27.7579 | YES | 12
8 | 0.84 | 75 | 63 | 12 | 7.1 | 34.4916 | YES | 12
9 | 0.96 | 75 | 72 | 12 | 7.5 | 40.1193 | YES | 12
10 | 0.9 | 75 | 67.5 | 12 | 7.4 | 38.4924 | YES | 12
11 | 0.93 | 75 | 69.75 | 12 | 7.1 | 34.8339 | YES | 12
12 | 0.87 | 75 | 65.25 | 12 | 7 | 33.4467 | YES | 12
13 | 0.74 | 75 | 55.5 | 12 | 7.3 | 36.5331 | YES | 12
14 | 0.84 | 75 | 63 | 12 | 7.2 | 35.6917 | YES | 12
15 | 0.83 | 75 | 62.25 | 14 | 7.1 | 29.6419 | YES | 12
16 | 0.84 | 75 | 63 | 14 | 7 | 28.5946 | YES | 12
17 | 0.77 | 75 | 57.75 | 14 | 7.1 | 29.4397 | YES | 12
18 | 1.12 | 75 | 84 | 14 | 7 | 29.523 | YES | 12
19 | 1.18 | 75 | 88.5 | 14 | 7.1 | 30.8485 | YES | 12
20 | 1.7 | 75 | 127.5 | 14 | 7.1 | 32.7299 | YES | 12
21 | 1.69 | 75 | 126.75 | 14 | 7.1 | 32.6927 | YES | 12
22 | 1.3 | 75 | 97.5 | 14 | 7.1 | 31.2731 | YES | 12
23 | 1.26 | 75 | 94.5 | 16 | 7.5 | 31.5943 | YES | 12
24 | 1.22 | 75 | 91.5 | 16 | 6.7 | 23.3569 | YES | 12
25 | 1.11 | 75 | 83.25 | 18 | 6.5 | 18.6919 | YES | 12
26 | 0.57 | 75 | 42.75 | 16 | 6.7 | 21.6743 | YES | 12
27 | 0.59 | 75 | 44.25 | 16 | 6.6 | 20.9251 | YES | 12
28 | 0.6 | 75 | 45 | 16 | 6.6 | 20.9492 | YES | 12
29 | 0.56 | 75 | 42 | 16 | 6.2 | 17.9392 | YES | 12
30 | 0.97 | 75 | 72.75 | 16 | 6.6 | 21.8617 | YES | 12
31 | 1.64 | 75 | 123 | 16 | 6.6 | 23.6126 | YES | 12
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2