## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | August 2022
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 5 | 0.027 | 0.027
2 | 22 | 22 | 0 | 5 | 0.031 | 0.031
3 | 21 | 21 | 0 | 5 | 0.023 | 0.023
4 | 0 | 0 | 0 | 5 | 0.02 | 0.02
5 | 22 | 22 | 0 | 5 | 0.022 | 0.022
6 | 22 | 22 | 1 | 5 | 0.009 | 0.009
7 | 22 | 22 | 0 | 5 | 0.027 | 0.027
8 | 22 | 22 | 0 | 5 | 0.013 | 0.013
9 | 22 | 22 | 0 | 5 | 0.012 | 0.012
10 | 22 | 22 | 0 | 5 | 0.014 | 0.014
11 | 21 | 21 | 0 | 5 | 0.01 | 0.01
12 | 21 | 21 | 0 | 5 | 0.012 | 0.012
13 | 21 | 21 | 0 | 5 | 0.012 | 0.012
14 | 22 | 22 | 0 | 5 | 0.013 | 0.013
15 | 21 | 21 | 0 | 5 | 0.013 | 0.013
16 | 20 | 20 | 0 | 5 | 0.013 | 0.013
17 | 21 | 21 | 0 | 5 | 0.012 | 0.012
18 | 20 | 20 | 0 | 5 | 0.012 | 0.012
19 | 20 | 20 | 0 | 5 | 0.012 | 0.014
20 | 16 | 16 | 0 | 5 | 0.014 | 0.014
21 | 16 | 16 | 0 | 5 | 0.012 | 0.012
22 | 21 | 21 | 0 | 5 | 0.012 | 0.012
23 | 21 | 21 | 0 | 5 | 0.013 | 0.013
24 | 20 | 20 | 0 | 5 | 0.012 | 0.012
25 | 0 | 0 | 0 | 5 | 0.012 | 0.012
26 | 19 | 19 | 0 | 5 | 0.012 | 0.012
27 | 19 | 19 | 0 | 5 | 0.012 | 0.012
28 | 21 | 21 | 0 | 5 | 0.012 | 0.012
29 | 20 | 20 | 0 | 5 | 0.012 | 0.012
30 | 20 | 20 | 0 | 5 | 0.013 | 0.013
31 | 20 | 20 | 0 | 5 | 0.012 | 0.012
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 09/07/2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
All daily turbidity readings ≤ 5 NTU?
June | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | August 2022 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.78 | 75 | 133.5 | 19 | 7.3 | 25.4689 | YES | 12
2 | 2.01 | 75 | 150.75 | 19 | 7.3 | 26.1486 | YES | 12
3 | 1.71 | 75 | 128.25 | 19 | 7.2 | 24.3407 | YES | 12
4 | 1.02 | 75 | 76.5 | 19 | 7.5 | 25.1512 | YES | 12
5 | 1.29 | 75 | 96.75 | 19 | 7.4 | 24.9925 | YES | 12
6 | 1.51 | 75 | 113.25 | 19 | 7.4 | 25.6305 | YES | 12
7 | 0.93 | 75 | 69.75 | 18 | 7.1 | 22.9307 | YES | 12
8 | 1.34 | 75 | 100.5 | 20 | 6.9 | 19.4867 | YES | 12
9 | 1.29 | 75 | 96.75 | 20 | 6.9 | 19.3743 | YES | 12
10 | 1.2 | 75 | 90 | 20 | 6.9 | 19.1736 | YES | 12
11 | 1.2 | 75 | 90 | 20 | 6.9 | 19.1736 | YES | 12
12 | 1.28 | 75 | 96 | 20 | 6.9 | 19.3519 | YES | 12
13 | 1.06 | 75 | 79.5 | 19 | 6.8 | 19.4424 | YES | 12
14 | 1.16 | 75 | 87 | 20 | 6.9 | 19.085 | YES | 12
15 | 1.73 | 75 | 129.75 | 20 | 7 | 21.1642 | YES | 12
16 | 2.13 | 75 | 159.75 | 20 | 7.2 | 23.8825 | YES | 12
17 | 1.62 | 75 | 121.5 | 20 | 7.2 | 22.5232 | YES | 12
18 | 1.67 | 75 | 125.25 | 20 | 7.2 | 22.6531 | YES | 12
19 | 1.38 | 75 | 103.5 | 20 | 7 | 20.3266 | YES | 12
20 | 1.79 | 75 | 134.25 | 20 | 6.9 | 20.5265 | YES | 12
21 | 1.81 | 75 | 135.75 | 20 | 6.9 | 20.574 | YES | 12
22 | 1.13 | 75 | 84.75 | 20 | 6.9 | 19.0189 | YES | 12
23 | 1.89 | 75 | 141.75 | 20 | 6.8 | 19.9996 | YES | 12
24 | 1.59 | 75 | 119.25 | 20 | 7.1 | 21.6208 | YES | 12
25 | 1.17 | 75 | 87.75 | 20 | 7 | 19.8395 | YES | 12
26 | 0.82 | 75 | 61.5 | 19 | 7.4 | 23.6806 | YES | 12
27 | 0.82 | 75 | 61.5 | 19 | 7.2 | 21.9743 | YES | 12
28 | 1.19 | 75 | 89.25 | 18 | 7.1 | 23.626 | YES | 12
29 | 2.05 | 75 | 153.75 | 18 | 7.5 | 30.2516 | YES | 12
30 | 1.6 | 75 | 120 | 18 | 7.2 | 25.7044 | YES | 12
31 | 1.26 | 75 | 94.5 | 18 | 7.1 | 23.8167 | YES | 12
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2