## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | September 2022
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 5 | 0.012 | 0.012
2 | 20 | 20 | 0 | 5 | 0.012 | 0.012
3 | 20 | 20 | 0 | 5 | 0.013 | 0.013
4 | 20 | 20 | 0 | 5 | 0.012 | 0.012
5 | 20 | 20 | 0 | 5 | 0.012 | 0.012
6 | 17 | 17 | 1 | 5 | 0.012 | 0.012
7 | 17 | 17 | 0 | 5 | 0.012 | 0.012
8 | 15 | 15 | 0 | 5 | 0.012 | 0.012
9 | 15 | 15 | 0 | 5 | 0.012 | 0.012
10 | 15 | 15 | 0 | 5 | 0.013 | 0.013
11 | 17 | 17 | 0 | 5 | 0.012 | 0.012
12 | 16 | 16 | 0 | 5 | 0.012 | 0.012
13 | 15 | 15 | 0 | 5 | 0.012 | 0.012
14 | 17 | 17 | 0 | 5 | 0.012 | 0.012
15 | 15 | 15 | 0 | 5 | 0.012 | 0.012
16 | 15 | 15 | 0 | 5 | 0.028 | 0.028
17 | 15 | 15 | 0 | 5 | 0.012 | 0.012
18 | 15 | 15 | 0 | 5 | 0.012 | 0.012
19 | 12 | 12 | 0 | 5 | 0.014 | 0.014
20 | 13 | 13 | 0 | 5 | 0.012 | 0.012
21 | 12 | 12 | 0 | 5 | 0.012 | 0.012
22 | 18 | 18 | 0 | 5 | 0.012 | 0.012
23 | 18 | 18 | 0 | 5 | 0.012 | 0.012
24 | 18 | 18 | 0 | 5 | 0.012 | 0.014
25 | 22 | 22 | 0 | 5 | 0.014 | 0.012
26 | 22 | 22 | 0 | 5 | 0.012 | 0.012
27 | 22 | 22 | 0 | 5 | 0.012 | 0.012
28 | 22 | 22 | 0 | 5 | 0.013 | 0.013
29 | 22 | 22 | 0 | 5 | 0.012 | 0.012
30 | 22 | 22 | 0 | 5 | 0.012 | 0.012
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 10/09/2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
All daily turbidity readings ≤ 5 NTU?
September | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | September 2022 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 75 | 90 | 18 | 7.2 | 24.5526 | YES | 12
2 | 0.48 | 75 | 36 | 18 | 6.8 | 19.455 | YES | 12
3 | 1.5 | 75 | 112.5 | 18 | 7.2 | 25.4117 | YES | 12
4 | 2.1 | 75 | 157.5 | 18 | 7.1 | 26.2239 | YES | 12
5 | 2.2 | 75 | 165 | 20 | 7.3 | 24.9902 | YES | 12
6 | 1.4 | 75 | 105 | 20 | 7.1 | 21.1526 | YES | 12
7 | 0.67 | 75 | 50.25 | 20 | 7.1 | 19.4426 | YES | 12
8 | 1.19 | 75 | 89.25 | 20 | 7.1 | 20.6464 | YES | 12
9 | 1.78 | 75 | 133.5 | 22 | 7.1 | 19.3056 | YES | 12
10 | 1.48 | 75 | 111 | 20 | 7.2 | 22.1633 | YES | 12
11 | 1.75 | 75 | 131.25 | 20 | 7.2 | 22.8624 | YES | 12
12 | 1.04 | 75 | 78 | 18 | 7.5 | 26.9567 | YES | 12
13 | 0.92 | 75 | 69 | 20 | 6.8 | 17.8748 | YES | 12
14 | 0.87 | 75 | 65.25 | 18 | 7.1 | 22.7731 | YES | 12
15 | 0.44 | 75 | 33 | 18 | 7.1 | 21.6736 | YES | 12
16 | 1.75 | 75 | 131.25 | 18 | 6.8 | 22.5239 | YES | 12
17 | 1.1 | 75 | 82.5 | 18 | 6.8 | 20.8992 | YES | 12
18 | 0.67 | 75 | 50.25 | 18 | 6.7 | 19.153 | YES | 12
19 | 1.24 | 75 | 93 | 18 | 6.7 | 20.4573 | YES | 12
20 | 0.7 | 75 | 52.5 | 18 | 6.7 | 19.2196 | YES | 12
21 | 0.58 | 75 | 43.5 | 18 | 6.8 | 19.6813 | YES | 12
22 | 0.91 | 75 | 68.25 | 18 | 6.8 | 20.446 | YES | 12
23 | 1.1 | 75 | 82.5 | 18 | 6.8 | 20.8992 | YES | 12
24 | 0.78 | 75 | 58.5 | 18 | 6.8 | 20.1414 | YES | 12
25 | 1.37 | 75 | 102.75 | 18 | 6.9 | 22.3824 | YES | 12
26 | 2.2 | 75 | 165 | 18 | 6.8 | 23.7193 | YES | 12
27 | 1.41 | 75 | 105.75 | 18 | 6.9 | 22.4856 | YES | 12
28 | 1.56 | 75 | 117 | 18 | 6.9 | 22.8769 | YES | 12
29 | 1.59 | 75 | 119.25 | 18 | 6.9 | 22.9559 | YES | 12
30 | 1.49 | 75 | 111.75 | 18 | 6.9 | 22.6935 | YES | 12
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2