## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | June 2023
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 | 18 | 0 | 5 | 0.014 | 0.014
2 | 18 | 18 | 0 | 5 | 0.014 | 0.014
3 | 16 | 16 | 0 | 5 | 0.013 | 0.013
4 | 16 | 16 | 0 | 5 | 0.013 | 0.013
5 | 22 | 22 | 0 | 5 | 0.012 | 0.012
6 | 0 | 0 | 0 | 5 | 0.057 | 0.057
7 | 22 | 22 | 0 | 5 | 0.013 | 0.013
8 | 23 | 23 | 0 | 5 | 0.012 | 0.012
9 | 22 | 22 | 0 | 5 | 0.04 | 0.04
10 | 22 | 22 | 0 | 5 | 0.012 | 0.012
11 | 22 | 21 | 1 | 5 | 0.013 | 0.013
12 | 20 | 19 | 1 | 5 | 0.012 | 0.012
13 | 15 | 15 | 0 | 5 | 0.012 | 0.012
14 | 15 | 15 | 0 | 5 | 0.012 | 0.012
15 | 23 | 22 | 1 | 5 | 0.013 | 0.013
16 | 0 | 0 | 0 | 5 | 0.049 | 0.049
17 | 22 | 21 | 1 | 5 | 0.013 | 0.013
18 | 22 | 21 | 1 | 5 | 0.012 | 0.012
19 | 0 | 0 | 0 | 5 | 0.018 | 0.018
20 | 0 | 0 | 0 | 5 | 0.039 | 0.037
21 | 20 | 20 | 0 | 5 | 0.012 | 0.012
22 | 0 | 0 | 0 | 5 | 0.017 | 0.017
23 | 23 | 22 | 1 | 5 | 0.02 | 0.02
24 | 0 | 0 | 0 | 5 | 0.034 | 0.034
25 | 0 | 0 | 0 | 5 | 0.029 | 0.029
26 | 22 | 22 | 0 | 5 | 0.012 | 0.012
27 | 20 | 20 | 0 | 5 | 0.052 | 0.052
28 | 0 | 0 | 0 | 5 | 0.012 | 0.012
29 | 0 | 0 | 0 | 5 | 0.013 | 0.013
30 | 20 | 20 | 0 | 5 | 0.012 | 0.012
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 07/08/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
June | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | June 2023 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.8 | 24 | 43.2 | 16 | 6.9 | 26.8946 | YES | 12
2 | 1.72 | 24 | 41.28 | 16 | 6.9 | 26.6496 | YES | 12
3 | 1.55 | 24 | 37.2 | 16 | 6.9 | 26.1362 | YES | 12
4 | 1.45 | 24 | 34.8 | 16 | 6.9 | 25.8387 | YES | 12
5 | 1.97 | 24 | 47.28 | 16 | 7.4 | 33.0085 | YES | 12
6 | 2.2 | 24 | 52.8 | 16 | 7.4 | 33.8832 | YES | 12
7 | 1.33 | 24 | 31.92 | 15 | 7.1 | 29.3539 | YES | 12
8 | 2.4 | 24 | 57.6 | 16.5 | 7.4 | 33.5276 | YES | 12
9 | 2.2 | 24 | 52.8 | 16 | 7 | 29.2176 | YES | 12
10 | 1.55 | 24 | 37.2 | 18 | 7 | 23.7205 | YES | 12
11 | 1.68 | 24 | 40.32 | 17 | 7 | 25.749 | YES | 12
12 | 1.52 | 24 | 36.48 | 18 | 7.3 | 26.4362 | YES | 12
13 | 1.95 | 24 | 46.8 | 17 | 7 | 26.5572 | YES | 12
14 | 1.65 | 24 | 39.6 | 16 | 7.4 | 31.8282 | YES | 12
15 | 2.2 | 24 | 52.8 | 17 | 7.1 | 28.362 | YES | 12
16 | 2.15 | 24 | 51.6 | 17 | 7.6 | 33.9405 | YES | 12
17 | 1.76 | 24 | 42.24 | 18 | 7.3 | 27.172 | YES | 12
18 | 1.74 | 24 | 41.76 | 17 | 7 | 25.9265 | YES | 12
19 | 1.57 | 24 | 37.68 | 17 | 7.2 | 27.3914 | YES | 12
20 | 1.79 | 24 | 42.96 | 17 | 7.4 | 30.2528 | YES | 12
21 | 2.2 | 24 | 52.8 | 17 | 7.3 | 30.5466 | YES | 12
22 | 1.47 | 24 | 35.28 | 17 | 7.3 | 28.1055 | YES | 12
23 | 1.3 | 24 | 31.2 | 17 | 7.4 | 28.6081 | YES | 12
24 | 1.78 | 24 | 42.72 | 17 | 7.3 | 29.118 | YES | 12
25 | 1.56 | 24 | 37.44 | 17 | 7.5 | 30.583 | YES | 12
26 | 1.92 | 24 | 46.08 | 18 | 7 | 24.7493 | YES | 12
27 | 2.4 | 24 | 57.6 | 18 | 6.7 | 23.3806 | YES | 12
28 | 2.4 | 24 | 57.6 | 18 | 7 | 26.1483 | YES | 12
29 | 2.4 | 24 | 57.6 | 18 | 6.8 | 24.2701 | YES | 12
30 | 2.4 | 24 | 57.6 | 18 | 6.8 | 24.2701 | YES | 12
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2