## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | July 2023
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 20 | 0 | 5 | 0.012 | 0.012
2 | 21 | 21 | 0 | 5 | 0.013 | 0.013
3 | 20 | 20 | 0 | 5 | 0.012 | 0.013
4 | 20 | 20 | 0 | 5 | 0.012 | 0.012
5 | 20 | 20 | 0 | 5 | 0.012 | 0.012
6 | 19 | 19 | 0 | 5 | 0.012 | 0.012
7 | 18 | 18 | 0 | 5 | 0.012 | 0.012
8 | 19 | 19 | 0 | 5 | 0.012 | 0.012
9 | 18 | 18 | 0 | 5 | 0.012 | 0.012
10 | 18 | 18 | 0 | 5 | 0.014 | 0.014
11 | 18 | 18 | 0 | 5 | 0.012 | 0.012
12 | 18 | 18 | 0 | 5 | 0.012 | 0.012
13 | 18 | 18 | 0 | 5 | 0.012 | 0.012
14 | 18 | 18 | 0 | 5 | 0.013 | 0.013
15 | 18 | 18 | 0 | 5 | 0.012 | 0.012
16 | 18 | 18 | 0 | 5 | 0.017 | 0.017
17 | 16 | 16 | 0 | 5 | 0.018 | 0.018
18 | 22 | 21 | 1 | 5 | 0.019 | 0.019
19 | 0 | 0 | 0 | 5 | 0.014 | 0.014
20 | 21 | 20 | 1 | 5 | 0.012 | 0.012
21 | 20 | 20 | 0 | 5 | 0.014 | 0.014
22 | 0 | 0 | 0 | 5 | 0.072 | 0.072
23 | 23 | 21 | 2 | 5 | 0.013 | 0.013
24 | 23 | 21 | 2 | 5 | 0.013 | 0.013
25 | 0 | 0 | 0 | 5 | 0.02 | 0.02
26 | 0 | 0 | 0 | 5 | 0.018 | 0.018
27 | 0 | 0 | 0 | 5 | 0.037 | 0.037
28 | 0 | 0 | 0 | 5 | 0.018 | 0.018
29 | 22 | 20 | 2 | 5 | 0.015 | 0.015
30 | 21 | 20 | 1 | 5 | 0.037 | 0.037
31 | 0 | 0 | 0 | 5 | 0.118 | 0.118
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 08/05/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
July | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | July 2023 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.19 | 24 | 52.56 | 18 | 7 | 25.527 | YES | 12
2 | 2.11 | 24 | 50.64 | 18 | 7.5 | 30.4592 | YES | 12
3 | 1.56 | 24 | 37.44 | 19 | 7.5 | 26.7553 | YES | 12
4 | 1.68 | 24 | 40.32 | 19 | 7.5 | 27.125 | YES | 12
5 | 1.88 | 24 | 45.12 | 18 | 7.2 | 26.5416 | YES | 12
6 | 1.58 | 24 | 37.92 | 18 | 7.7 | 30.8802 | YES | 12
7 | 1.42 | 24 | 34.08 | 18 | 7.8 | 31.4668 | YES | 12
8 | 1.7 | 24 | 40.8 | 18 | 7.7 | 31.3052 | YES | 12
9 | 1.55 | 24 | 37.2 | 18 | 7.6 | 29.6547 | YES | 12
10 | 2.4 | 24 | 57.6 | 18 | 7.3 | 29.2326 | YES | 12
11 | 1.74 | 24 | 41.76 | 18 | 7.4 | 28.1365 | YES | 12
12 | 1.51 | 24 | 36.24 | 18 | 7.4 | 27.4067 | YES | 12
13 | 1.49 | 24 | 35.76 | 18 | 7.3 | 26.3456 | YES | 12
14 | 1.8 | 24 | 43.2 | 18 | 7.3 | 27.2965 | YES | 12
15 | 2.2 | 24 | 52.8 | 19 | 7.6 | 29.8733 | YES | 12
16 | 2.2 | 24 | 52.8 | 19 | 7.4 | 27.7357 | YES | 12
17 | 1.73 | 24 | 41.52 | 21 | 7.4 | 22.9806 | YES | 12
18 | 2.2 | 24 | 52.8 | 21 | 7.5 | 25.1767 | YES | 12
19 | 1.92 | 24 | 46.08 | 19 | 7.4 | 26.8619 | YES | 12
20 | 1.64 | 24 | 39.36 | 19 | 7.5 | 27.0012 | YES | 12
21 | 1.23 | 24 | 29.52 | 19 | 7.4 | 24.8212 | YES | 12
22 | 1.27 | 24 | 30.48 | 19 | 7.3 | 24.0222 | YES | 12
23 | 1.31 | 24 | 31.44 | 19 | 7.3 | 24.1328 | YES | 12
24 | 1.16 | 24 | 27.84 | 19 | 7.2 | 22.8508 | YES | 12
25 | 1.07 | 24 | 25.68 | 19 | 7.2 | 22.6155 | YES | 12
26 | 1.13 | 24 | 27.12 | 19 | 7.5 | 25.4702 | YES | 12
27 | 1.16 | 24 | 27.84 | 19 | 7.1 | 22.0117 | YES | 12
28 | 1.02 | 24 | 24.48 | 19 | 7.1 | 21.6597 | YES | 12
29 | 1.25 | 24 | 30 | 19 | 7.5 | 25.8227 | YES | 12
30 | 1.45 | 24 | 34.8 | 19 | 7.2 | 23.625 | YES | 12
31 | 1.5 | 24 | 36 | 19 | 7.6 | 27.5791 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2