## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | October 2023
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 5 | 0.16 | 0.16
2 | 0 | 0 | 0 | 5 | 0.183 | 0.183
3 | 0 | 0 | 0 | 5 | 0.157 | 0.157
4 | 0 | 0 | 0 | 5 | 0.168 | 0.168
5 | 0 | 0 | 0 | 5 | 0.19 | 0.19
6 | 0 | 0 | 0 | 5 | 0.184 | 0.184
7 | 17 | 15 | 2 | 5 | 0.064 | 0.064
8 | 0 | 0 | 0 | 5 | 0.091 | 0.091
9 | 0 | 0 | 0 | 5 | 0.067 | 0.067
10 | 18 | 17 | 1 | 5 | 0.056 | 0.056
11 | 0 | 0 | 0 | 5 | 0.054 | 0.086
12 | 0 | 0 | 0 | 5 | 0.054 | 0.054
13 | 0 | 0 | 0 | 5 | 0.12 | 0.054
14 | 18 | 17 | 1 | 5 | 0.012 | 0.12
15 | 0 | 0 | 0 | 5 | 0.012 | 0.012
16 | 0 | 0 | 0 | 5 | 0.012 | 0.012
17 | 0 | 0 | 0 | 5 | 0.012 | 0.012
18 | 26 | 25 | 1 | 5 | 0.012 | 0.012
19 | 16 | 16 | 0 | 5 | 0.012 | 0.012
20 | 16 | 16 | 0 | 5 | 0.012 | 0.012
21 | 0 | 0 | 0 | 5 | 0.015 | 0.015
22 | 0 | 0 | 0 | 5 | 0.057 | 0.057
23 | 0 | 0 | 0 | 5 | 0.012 | 0.012
24 | 0 | 0 | 0 | 5 | 0.041 | 0.041
25 | 18 | 18 | 0 | 5 | 0.012 | 0.012
26 | 18 | 18 | 0 | 5 | 0.043 | 0.043
27 | 0 | 0 | 0 | 5 | 0.012 | 0.012
28 | 18 | 18 | 0 | 5 | 0.012 | 0.012
29 | 16 | 16 | 0 | 5 | 0.011 | 0.011
30 | 0 | 0 | 0 | 5 | 0.045 | 0.045
31 | 20 | 19 | 1 | 5 | 0.012 | 0.012
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | No | No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 11/08/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
REVISED 12/14/2023 due to using
correspond to continuous readings' maximum. NOTE: Failed to meet CT 10/12-16.
Failed to maintain Chlorine residual at .2 mg/l or greater 10/12, 14, 15.
October | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | October 2023 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 24 | 52.8 | 14 | 7 | 16.6935 | YES | 8
2 | 1.86 | 24 | 44.64 | 16 | 7 | 14.0526 | YES | 8
3 | 1.8 | 24 | 43.2 | 16 | 6.9 | 13.4473 | YES | 8
4 | 1.74 | 24 | 41.76 | 16 | 7.1 | 14.3858 | YES | 8
5 | 2.4 | 24 | 57.6 | 16 | 7 | 14.9459 | YES | 8
6 | 1.59 | 24 | 38.16 | 16 | 6.8 | 12.6481 | YES | 8
7 | 1.41 | 24 | 33.84 | 17 | 6.8 | 11.5844 | YES | 8
8 | 1.3 | 24 | 31.2 | 17 | 6.8 | 11.4389 | YES | 8
9 | 1.29 | 24 | 30.96 | 17 | 6.9 | 11.8608 | YES | 8
10 | 1.8 | 24 | 43.2 | 17 | 7.1 | 13.5474 | YES | 8
11 | 1.23 | 24 | 29.52 | 16.3 | 7.3 | 14.3281 | YES | 8
12 | 0.07 | 24 | 1.68 | 16 | 7.2 | 12.3344 | NO | 8
13 | 0.21 | 24 | 5.04 | 15 | 7.2 | 13.4032 | NO | 8
14 | 0.012 | 24 | 0.288 | 15 | 7.1 | 12.6239 | NO | 8
15 | 0.015 | 24 | 0.36 | 17 | 7.1 | 11.039 | NO | 8
16 | 0.34 | 24 | 8.16 | 16 | 6.8 | 10.9566 | NO | 8
17 | 0.59 | 24 | 14.16 | 15.3 | 6.6 | 10.9686 | YES | 8
18 | 0.71 | 24 | 17.04 | 16 | 6.7 | 11.0133 | YES | 8
19 | 0.97 | 24 | 23.28 | 16 | 6.7 | 11.3477 | YES | 8
20 | 0.82 | 24 | 19.68 | 17 | 6.6 | 10.0418 | YES | 8
21 | 0.81 | 24 | 19.44 | 16 | 7 | 12.4617 | YES | 8
22 | 1.23 | 24 | 29.52 | 17 | 7 | 12.2273 | YES | 8
23 | 1.13 | 24 | 27.12 | 16 | 7 | 12.9271 | YES | 8
24 | 1.05 | 24 | 25.2 | 16 | 7 | 12.8092 | YES | 8
25 | 0.83 | 24 | 19.92 | 15 | 6.8 | 12.3978 | YES | 8
26 | 0.85 | 24 | 20.4 | 15 | 6.8 | 12.4262 | YES | 8
27 | 0.82 | 24 | 19.68 | 15 | 6.8 | 12.3836 | YES | 8
28 | 0.73 | 24 | 17.52 | 15 | 6.9 | 12.722 | YES | 8
29 | 0.87 | 24 | 20.88 | 14 | 6.8 | 13.3186 | YES | 8
30 | 0.9 | 24 | 21.6 | 14 | 7.1 | 14.9397 | YES | 8
31 | 1.18 | 24 | 28.32 | 14 | 7.1 | 15.4242 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2