## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | November 2023
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 19 | 19 | 0 | 5 | 0.012 | 0.012
2 | 0 | 0 | 0 | 5 | 0.057 | 0.057
3 | 0 | 0 | 0 | 5 | 0.046 | 0.046
4 | 0 | 0 | 0 | 5 | 0.053 | 0.053
5 | 19 | 19 | 0 | 5 | 0.012 | 0.012
6 | 0 | 0 | 0 | 5 | 0.072 | 0.072
7 | 0 | 0 | 0 | 5 | 0.061 | 0.061
8 | 0 | 0 | 0 | 5 | 0.049 | 0.049
9 | 0 | 0 | 0 | 5 | 0.043 | 0.043
10 | 15 | 15 | 0 | 5 | 0.045 | 0.045
11 | 17 | 15 | 2 | 5 | 0.013 | 0.013
12 | 17 | 16 | 1 | 5 | 0.014 | 0.014
13 | 0 | 0 | 0 | 5 | 0.053 | 0.052
14 | 0 | 0 | 0 | 5 | 0.014 | 0.014
15 | 20 | 20 | 0 | 5 | 0.016 | 0.016
16 | 20 | 20 | 0 | 5 | 0.014 | 0.014
17 | 20 | 20 | 0 | 5 | 0.013 | 0.014
18 | 20 | 20 | 0 | 5 | 0.013 | 0.013
19 | 22 | 20 | 2 | 5 | 0.013 | 0.013
20 | 19 | 18 | 1 | 5 | 0.013 | 0.013
21 | 0 | 0 | 0 | 5 | 0.012 | 0.012
22 | 0 | 0 | 0 | 5 | 0.046 | 0.046
23 | 0 | 0 | 0 | 5 | 0.018 | 0.018
24 | 0 | 0 | 0 | 5 | 0.029 | 0.029
25 | 20 | 20 | 0 | 5 | 0.017 | 0.017
26 | 0 | 0 | 0 | 5 | 0.046 | 0.046
27 | 0 | 0 | 0 | 5 | 0.038 | 0.038
28 | 0 | 0 | 0 | 5 | 0.012 | 0.012
29 | 0 | 0 | 0 | 5 | 0.11 | 0.11
30 | 0 | 0 | 0 | 5 | 0.043 | 0.043
Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 12/05/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
ui
correspond to continuous readings' maximum. NOTE: REVISED 12/14/2023 due to using wrong Giardia Log Inactivation
data. System meets 2.5 log inactivation, requiring .5 log inactivation for Chlorine. Corrected...
November | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | November 2023 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.25 | 24 | 30 | 14 | 6.9 | 14.4363 | YES | 8
2 | 1.28 | 24 | 30.72 | 15 | 7 | 14.0616 | YES | 8
3 | 1.22 | 24 | 29.28 | 15 | 6.9 | 13.4559 | YES | 8
4 | 1.18 | 24 | 28.32 | 16 | 6.9 | 12.5258 | YES | 8
5 | 1.18 | 24 | 28.32 | 16 | 6.8 | 12.0672 | YES | 8
6 | 0.81 | 24 | 19.44 | 16 | 6.7 | 11.1407 | YES | 8
7 | 1.02 | 24 | 24.48 | 14 | 6.7 | 13.0542 | YES | 8
8 | 0.94 | 24 | 22.56 | 13 | 6.7 | 13.8313 | YES | 8
9 | 0.91 | 24 | 21.84 | 13 | 6.6 | 13.2808 | YES | 8
10 | 0.91 | 24 | 21.84 | 13 | 6.8 | 14.3057 | YES | 8
11 | 0.68 | 24 | 16.32 | 13 | 6.7 | 13.4263 | YES | 8
12 | 0.87 | 24 | 20.88 | 13 | 6.6 | 13.2201 | YES | 12
13 | 1.1 | 24 | 26.4 | 13 | 6.8 | 14.6193 | YES | 8
14 | 1.05 | 24 | 25.2 | 13 | 6.7 | 14.0063 | YES | 8
15 | 0.98 | 24 | 23.52 | 14 | 6.9 | 13.998 | YES | 8
16 | 0.92 | 24 | 22.08 | 13 | 6.9 | 14.8635 | YES | 8
17 | 0.94 | 24 | 22.56 | 13 | 7 | 15.4601 | YES | 8
18 | 0.93 | 24 | 22.32 | 14 | 7 | 14.4449 | YES | 8
19 | 0.95 | 24 | 22.8 | 13 | 6.9 | 14.9144 | YES | 8
20 | 1.13 | 24 | 27.12 | 11.4 | 6.6 | 15.61 | YES | 8
21 | 1.12 | 24 | 26.88 | 12 | 6.6 | 15.0157 | YES | 8
22 | 1.22 | 24 | 29.28 | 12 | 6.6 | 15.1779 | YES | 8
23 | 1.39 | 24 | 33.36 | 12 | 6.6 | 15.4584 | YES | 8
24 | 1.73 | 24 | 41.52 | 11 | 6.5 | 16.5203 | YES | 8
25 | 1.27 | 24 | 30.48 | 10 | 6.6 | 17.3254 | YES | 8
26 | 1.69 | 24 | 40.56 | 10 | 6.8 | 19.4417 | YES | 8
27 | 1.44 | 24 | 34.56 | 10 | 6.8 | 18.9088 | YES | 8
28 | 1.75 | 24 | 42 | 10 | 6.8 | 19.5721 | YES | 8
29 | 1.72 | 24 | 41.28 | 10 | 6.8 | 19.5068 | YES | 8
30 | 1.3 | 24 | 31.2 | 10 | 6.8 | 18.6175 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2