## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | January 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 5 | 0.053 | 0.053
2 | 0 | 0 | 0 | 5 | 0.048 | 0.048
3 | 0 | 0 | 0 | 5 | 0.051 | 0.051
4 | 0 | 0 | 0 | 5 | 0.054 | 0.054
5 | 0 | 0 | 0 | 5 | 0.012 | 0.012
6 | 0 | 0 | 0 | 5 | 0.018 | 0.018
7 | 0 | 0 | 0 | 5 | 0.012 | 0.012
8 | 0 | 0 | 0 | 5 | 0.068 | 0.068
9 | 0 | 0 | 0 | 5 | 0.055 | 0.055
10 | 0 | 0 | 0 | 5 | 0.047 | 0.047
11 | 0 | 0 | 0 | 5 | 0.026 | 0.026
12 | 0 | 0 | 0 | 5 | 0.05 | 0.05
13 | 0 | 0 | 0 | 5 | 0.024 | 0.024
14 | 0 | 0 | 0 | 5 | 0.016 | 0.016
15 | 17 | 16 | 1 | 5 | 0.059 | 0.059
16 | 15 | 15 | 0 | 5 | 0.05 | 0.05
17 | 17 | 16 | 1 | 5 | 0.012 | 0.012
18 | 0 | 0 | 0 | 5 | 0.059 | 0.059
19 | 17 | 16 | 1 | 5 | 0.014 | 0.014
20 | 16 | 15 | 1 | 5 | 0.017 | 0.017
21 | 20 | 20 | 0 | 5 | 0.013 | 0.013
22 | 20 | 20 | 0 | 5 | 0.013 | 0.013
23 | 0 | 0 | 0 | 5 | 0.057 | 0.057
24 | 16 | 16 | 0 | 5 | 0.012 | 0.012
25 | 0 | 0 | 0 | 5 | 0.112 | 0.112
26 | 0 | 0 | 0 | 5 | 0.051 | 0.051
27 | 22 | 22 | 0 | 5 | 0.013 | 0.013
28 | 0 | 0 | 0 | 5 | 0.069 | 0.069
29 | 18 | 18 | 0 | 5 | 0.012 | 0.012
30 | 0 | 0 | 0 | 5 | 0.069 | 0.069
31 | 18 | 18 | 0 | 5 | 0.012 | 0.012
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 2/06/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
ui
correspond to continuous readings' maximum.
January | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | January 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.76 | 24 | 42.24 | 12 | 6.8 | 17.2201 | YES | 8
2 | 1.65 | 24 | 39.6 | 12 | 6.8 | 17.0139 | YES | 8
3 | 2 | 24 | 48 | 12 | 6.9 | 18.2973 | YES | 8
4 | 2.05 | 24 | 49.2 | 12 | 6.9 | 18.3987 | YES | 8
5 | 1.9 | 24 | 45.6 | 12 | 6.9 | 18.0963 | YES | 8
6 | 2 | 24 | 48 | 12 | 6.8 | 17.68 | YES | 8
7 | 1.23 | 24 | 29.52 | 10 | 6.9 | 19.1225 | YES | 8
8 | 2.2 | 24 | 52.8 | 10 | 7.2 | 23.6904 | YES | 8
9 | 1.46 | 24 | 35.04 | 10 | 7 | 20.3126 | YES | 8
10 | 1.47 | 24 | 35.28 | 10 | 7 | 20.3353 | YES | 8
11 | 2.28 | 24 | 54.72 | 10 | 7.1 | 23.0759 | YES | 8
12 | 2.2 | 24 | 52.8 | 10 | 7.1 | 22.8674 | YES | 12
13 | 2.2 | 24 | 52.8 | 10 | 7.2 | 23.6904 | YES | 8
14 | 2.2 | 24 | 52.8 | 10 | 6.7 | 19.8776 | YES | 8
15 | 2.2 | 24 | 52.8 | 11 | 6.7 | 18.6274 | YES | 8
16 | 1.4 | 24 | 33.6 | 11 | 6.7 | 17.0564 | YES | 8
17 | 1.29 | 24 | 30.96 | 11 | 6.7 | 16.8524 | YES | 8
18 | 1.27 | 24 | 30.48 | 11 | 6.8 | 17.3986 | YES | 8
19 | 1.22 | 24 | 29.28 | 11 | 6.6 | 16.1669 | YES | 8
20 | 1.04 | 24 | 24.96 | 11 | 6.6 | 15.8543 | YES | 8
21 | 2.14 | 24 | 51.36 | 11 | 6.9 | 19.8297 | YES | 8
22 | 2.2 | 24 | 52.8 | 14 | 6.3 | 12.8748 | YES | 8
23 | 2.2 | 24 | 52.8 | 14 | 6.5 | 13.8693 | YES | 8
24 | 1.92 | 24 | 46.08 | 12 | 6.3 | 14.8021 | YES | 8
25 | 1.57 | 24 | 37.68 | 12 | 6.8 | 16.8657 | YES | 8
26 | 0.57 | 24 | 13.68 | 14 | 6.2 | 10.2834 | YES | 8
27 | 2.2 | 24 | 52.8 | 13 | 6.9 | 17.195 | YES | 8
28 | 2.2 | 24 | 52.8 | 14 | 6.4 | 13.363 | YES | 8
29 | 2.2 | 24 | 52.8 | 12 | 6.4 | 15.7749 | YES | 8
30 | 1.3 | 24 | 31.2 | 12.7 | 6.6 | 14.1679 | YES | 8
31 | 1.83 | 24 | 43.92 | 11.6 | 6.1 | 14.0653 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2