## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | February 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 16 | 16 | 0 | 5 | 0.023 | 0.023
2 | 0 | 0 | 0 | 5 | 0.013 | 0.013
3 | 17 | 17 | 0 | 5 | 0.013 | 0.013
4 | 15 | 15 | 0 | 5 | 0.023 | 0.023
5 | 0 | 0 | 0 | 5 | 0.012 | 0.012
6 | 0 | 0 | 0 | 5 | 0.012 | 0.012
7 | 0 | 0 | 0 | 5 | 0.017 | 0.017
8 | 16 | 16 | 0 | 5 | 0.012 | 0.012
9 | 0 | 0 | 0 | 5 | 0.012 | 0.012
10 | 15 | 15 | 0 | 5 | 0.016 | 0.016
11 | 20 | 20 | 0 | 5 | 0.017 | 0.017
12 | 0 | 0 | 0 | 5 | 0.044 | 0.044
13 | 0 | 0 | 0 | 5 | 0.032 | 0.032
14 | 0 | 0 | 0 | 5 | 0.016 | 0.016
15 | 19 | 19 | 0 | 5 | 0.012 | 0.012
16 | 19 | 19 | 0 | 5 | 0.012 | 0.012
17 | 0 | 0 | 0 | 5 | 0.012 | 0.012
18 | 0 | 0 | 0 | 5 | 0.038 | 0.038
19 | 0 | 0 | 0 | 5 | 0.016 | 0.016
20 | 0 | 0 | 0 | 5 | 0.029 | 0.029
21 | 19 | 19 | 0 | 5 | 0.012 | 0.012
22 | 0 | 0 | 0 | 5 | 0.017 | 0.017
23 | 0 | 0 | 0 | 5 | 0.037 | 0.037
24 | 0 | 0 | 0 | 5 | 0.012 | 0.012
25 | 0 | 0 | 0 | 5 | 0.016 | 0.016
26 | 16 | 15 | 1 | 5 | 0.014 | 0.014
27 | 15 | 15 | 0 | 5 | 0.012 | 0.012
28 | 15 | 15 | 0 | 5 | 0.014 | 0.014
29 | 16 | 16 | 0 | 5 | 0.012 | 0.012
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 3/08/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
ui
correspond to continuous readings' maximum.
February | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | February 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.45 | 24 | 34.8 | 11.2 | 6.1 | 13.8487 | YES | 8
2 | 1.51 | 24 | 36.24 | 11.4 | 6.4 | 15.2073 | YES | 8
3 | 1.58 | 24 | 37.92 | 10.5 | 6.3 | 15.681 | YES | 8
4 | 2.14 | 24 | 51.36 | 9.9 | 6.8 | 20.5783 | YES | 8
5 | 2.16 | 24 | 51.84 | 11.7 | 6.7 | 17.7268 | YES | 8
6 | 1.96 | 24 | 47.04 | 12 | 6.9 | 18.2166 | YES | 8
7 | 2.07 | 24 | 49.68 | 10.2 | 6.7 | 19.3381 | YES | 8
8 | 1.49 | 24 | 35.76 | 10.5 | 6.9 | 19.0546 | YES | 8
9 | 1.58 | 24 | 37.92 | 11.5 | 6.8 | 17.433 | YES | 8
10 | 1.81 | 24 | 43.44 | 13.12 | 6.9 | 16.3182 | YES | 8
11 | 1.67 | 24 | 40.08 | 12 | 7 | 18.2593 | YES | 8
12 | 1.44 | 24 | 34.56 | 12 | 6.7 | 16.0744 | YES | 12
13 | 1.48 | 24 | 35.52 | 12 | 6.7 | 16.1444 | YES | 8
14 | 1.75 | 24 | 42 | 12 | 6.9 | 17.7995 | YES | 8
15 | 1.82 | 24 | 43.68 | 12 | 6.9 | 17.9373 | YES | 8
16 | 1.2 | 24 | 28.8 | 12 | 6.9 | 16.7577 | YES | 8
17 | 2.2 | 24 | 52.8 | 12 | 6.9 | 18.7068 | YES | 8
18 | 1.89 | 24 | 45.36 | 12 | 6.7 | 16.8819 | YES | 8
19 | 1.97 | 24 | 47.28 | 12 | 6.9 | 18.2367 | YES | 8
20 | 2.17 | 24 | 52.08 | 12 | 6.5 | 16.2634 | YES | 8
21 | 2.2 | 24 | 52.8 | 12 | 6.7 | 17.4652 | YES | 8
22 | 2.2 | 24 | 52.8 | 12 | 6.6 | 16.8797 | YES | 8
23 | 2.2 | 24 | 52.8 | 12 | 6.5 | 16.3166 | YES | 8
24 | 2.2 | 24 | 52.8 | 12 | 6.7 | 17.4652 | YES | 8
25 | 2.2 | 24 | 52.8 | 12 | 6.6 | 16.8797 | YES | 8
26 | 2.2 | 24 | 52.8 | 12 | 6.8 | 18.074 | YES | 8
27 | 2.2 | 24 | 52.8 | 12 | 6.7 | 17.4652 | YES | 8
28 | 2.2 | 24 | 52.8 | 12 | 6.5 | 16.3166 | YES | 8
29 | 2.2 | 24 | 52.8 | 12 | 6.7 | 17.4652 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2