## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | March 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 20 | 0 | 5 | 0.012 | 0.012
2 | 20 | 20 | 0 | 5 | 0.039 | 0.039
3 | 20 | 20 | 0 | 5 | 0.012 | 0.012
4 | 0 | 0 | 0 | 5 | 0.025 | 0.025
5 | 0 | 0 | 0 | 5 | 0.042 | 0.042
6 | 19 | 19 | 0 | 5 | 0.011 | 0.011
7 | 19 | 19 | 0 | 5 | 0.011 | 0.011
8 | 0 | 0 | 0 | 5 | 0.021 | 0.021
9 | 18 | 18 | 0 | 5 | 0.011 | 0.011
10 | 19 | 19 | 0 | 5 | 0.05 | 0.05
11 | 0 | 0 | 0 | 5 | 0.047 | 0.047
12 | 0 | 0 | 0 | 5 | 0.044 | 0.044
13 | 0 | 0 | 0 | 5 | 0.043 | 0.043
14 | 0 | 0 | 0 | 5 | 0.038 | 0.038
15 | 18 | 18 | 0 | 5 | 0.011 | 0.011
16 | 0 | 0 | 0 | 5 | 0.027 | 0.027
17 | 15 | 15 | 0 | 5 | 0.012 | 0.012
18 | 15 | 15 | 0 | 5 | 0.011 | 0.011
19 | 18 | 17 | 1 | 5 | 0.013 | 0.013
20 | 15 | 15 | 0 | 5 | 0.011 | 0.011
21 | 15 | 15 | 0 | 5 | 0.013 | 0.013
22 | 15 | 15 | 0 | 5 | 0.011 | 0.011
23 | 13 | 13 | 0 | 5 | 0.011 | 0.011
24 | 0 | 0 | 0 | 5 | 0.067 | 0.067
25 | 0 | 0 | 0 | 5 | 0.084 | 0.084
26 | 19 | 19 | 0 | 5 | 0.011 | 0.011
27 | 18 | 18 | 0 | 5 | 0.011 | 0.011
28 | 0 | 0 | 0 | 5 | 0.014 | 0.014
29 | 0 | 0 | 0 | 5 | 0.012 | 0.012
30 | 19 | 19 | 0 | 5 | 0.016 | 0.016
31 | 20 | 20 | 0 | 5 | 0.09 | 0.09
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 4/04/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
ui
correspond to continuous readings' maximum.
March | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | March 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 24 | 52.8 | 11 | 7.2 | 22.1718 | YES | 8
2 | 2.2 | 24 | 52.8 | 10 | 7 | 22.0758 | YES | 8
3 | 2.2 | 24 | 52.8 | 10 | 6.7 | 19.8776 | YES | 8
4 | 2.2 | 24 | 52.8 | 10 | 6.6 | 19.2 | YES | 8
5 | 1.59 | 24 | 38.16 | 10 | 6.8 | 19.2265 | YES | 8
6 | 1.61 | 24 | 38.64 | 10 | 6.8 | 19.2694 | YES | 8
7 | 1.3 | 24 | 31.2 | 10 | 6.4 | 16.2401 | YES | 8
8 | 1.72 | 24 | 41.28 | 10 | 6.6 | 18.2053 | YES | 8
9 | 1.83 | 24 | 43.92 | 10 | 6.6 | 18.428 | YES | 8
10 | 2.1 | 24 | 50.4 | 10 | 6.6 | 18.9879 | YES | 8
11 | 2.08 | 24 | 49.92 | 10 | 6.7 | 19.6132 | YES | 8
12 | 1.66 | 24 | 39.84 | 10 | 6.8 | 19.3769 | YES | 12
13 | 1.26 | 24 | 30.24 | 11 | 7.1 | 19.2685 | YES | 8
14 | 1.6 | 24 | 38.4 | 11 | 7 | 19.3303 | YES | 8
15 | 2.16 | 24 | 51.84 | 11 | 6.7 | 18.5451 | YES | 8
16 | 2.14 | 24 | 51.36 | 11 | 6.7 | 18.504 | YES | 8
17 | 2.2 | 24 | 52.8 | 11 | 6.7 | 18.6274 | YES | 8
18 | 2.18 | 24 | 52.32 | 12.4 | 6.2 | 14.3585 | YES | 8
19 | 2.2 | 24 | 52.8 | 11.4 | 6.2 | 15.3184 | YES | 8
20 | 2.2 | 24 | 52.8 | 11.8 | 6.3 | 15.447 | YES | 8
21 | 2.2 | 24 | 52.8 | 12.9 | 6 | 12.3948 | YES | 8
22 | 2.2 | 24 | 52.8 | 12.2 | 6.2 | 14.5696 | YES | 8
23 | 2.2 | 24 | 52.8 | 11.9 | 6.2 | 14.8453 | YES | 8
24 | 1.28 | 24 | 30.72 | 11.4 | 6.2 | 13.8845 | YES | 8
25 | 1.71 | 24 | 41.04 | 12 | 6.9 | 17.7213 | YES | 8
26 | 1.75 | 24 | 42 | 12.2 | 6.7 | 16.4156 | YES | 8
27 | 1.4 | 24 | 33.6 | 11.8 | 6.6 | 15.6715 | YES | 8
28 | 1.27 | 24 | 30.48 | 11.5 | 6.3 | 14.247 | YES | 8
29 | 1.48 | 24 | 35.52 | 11 | 6.4 | 15.5447 | YES | 8
30 | 1.44 | 24 | 34.56 | 11.7 | 6.8 | 16.9493 | YES | 8
31 | 1.29 | 24 | 30.96 | 11.5 | 6.5 | 15.2611 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2