## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | April 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 5 | 0.056 | 0.056
2 | 0 | 0 | 0 | 5 | 0.012 | 0.012
3 | 0 | 0 | 0 | 5 | 0.011 | 0.011
4 | 0 | 0 | 0 | 5 | 0.012 | 0.012
5 | 0 | 0 | 0 | 5 | 0.048 | 0.048
6 | 0 | 0 | 0 | 5 | 0.045 | 0.045
7 | 0 | 0 | 0 | 5 | 0.011 | 0.011
8 | 0 | 0 | 0 | 5 | 0.057 | 0.057
9 | 0 | 0 | 0 | 5 | 0.058 | 0.058
10 | 0 | 0 | 0 | 5 | 0.051 | 0.051
11 | 0 | 0 | 0 | 5 | 0.063 | 0.063
12 | 0 | 0 | 0 | 5 | 0.087 | 0.087
13 | 0 | 0 | 0 | 5 | 0.02 | 0.026
14 | 0 | 0 | 0 | 5 | 0.012 | 0.012
15 | 0 | 0 | 0 | 5 | 0.011 | 0.011
16 | 0 | 0 | 0 | 5 | 0.023 | 0.023
17 | 0 | 0 | 0 | 5 | 0.011 | 0.011
18 | 0 | 0 | 0 | 5 | 0.011 | 0.011
19 | 17 | 16 | 1 | 5 | 0.011 | 0.011
20 | 21 | 20 | 1 | 5 | 0.012 | 0.012
21 | 21 | 20 | 1 | 5 | 0.107 | 0.107
22 | 0 | 0 | 0 | 5 | 0.013 | 0.013
23 | 0 | 0 | 0 | 5 | 0.067 | 0.067
24 | 0 | 0 | 0 | 5 | 0.011 | 0.011
25 | 0 | 0 | 0 | 5 | 0.079 | 0.079
26 | 0 | 0 | 0 | 5 | 0.076 | 0.076
27 | 0 | 0 | 0 | 5 | 0.082 | 0.082
28 | 0 | 0 | 0 | 5 | 0.073 | 0.073
29 | 17 | 17 | 0 | 5 | 0.017 | 0.017
30 | 16 | 16 | 0 | 5 | 0.03 | 0.03
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 5/07/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
April | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | April 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.28 | 24 | 30.72 | 11.5 | 6.8 | 16.8694 | YES | 8
2 | 1.55 | 24 | 37.2 | 11.5 | 6.8 | 17.3757 | YES | 8
3 | 1.54 | 24 | 36.96 | 11.4 | 6.5 | 15.7776 | YES | 8
4 | 1.95 | 24 | 46.8 | 11.4 | 6.5 | 16.4959 | YES | 8
5 | 1.27 | 24 | 30.48 | 12 | 6.2 | 13.3662 | YES | 8
6 | 1.66 | 24 | 39.84 | 12 | 6.3 | 14.3965 | YES | 8
7 | 1.54 | 24 | 36.96 | 12 | 6.1 | 13.3084 | YES | 8
8 | 2.2 | 24 | 52.8 | 12 | 6.3 | 15.2539 | YES | 8
9 | 2.2 | 24 | 52.8 | 14 | 6.5 | 13.8693 | YES | 8
10 | 2.2 | 24 | 52.8 | 14 | 6.5 | 13.8693 | YES | 8
11 | 2.2 | 24 | 52.8 | 14 | 6.6 | 14.3941 | YES | 8
12 | 1.91 | 24 | 45.84 | 14 | 6.6 | 13.9252 | YES | 12
13 | 2.2 | 24 | 52.8 | 14 | 6.9 | 16.0872 | YES | 8
14 | 2.2 | 24 | 52.8 | 14 | 6.8 | 15.5023 | YES | 8
15 | 2.2 | 24 | 52.8 | 13 | 6.6 | 15.3882 | YES | 8
16 | 2.2 | 24 | 52.8 | 13 | 7.3 | 19.9296 | YES | 8
17 | 2.2 | 24 | 52.8 | 13 | 6.8 | 16.5709 | YES | 8
18 | 2.2 | 24 | 52.8 | 13 | 7 | 17.8421 | YES | 8
19 | 2.2 | 24 | 52.8 | 14 | 6.6 | 14.3941 | YES | 8
20 | 2.2 | 24 | 52.8 | 14 | 7.6 | 20.8295 | YES | 8
21 | 2.2 | 24 | 52.8 | 14 | 6.9 | 16.0872 | YES | 8
22 | 1.28 | 24 | 30.72 | 14 | 6.8 | 13.9578 | YES | 8
23 | 1.45 | 24 | 34.8 | 14 | 6.8 | 14.2314 | YES | 8
24 | 1.69 | 24 | 40.56 | 14 | 6.8 | 14.6267 | YES | 8
25 | 1.71 | 24 | 41.04 | 14 | 6.8 | 14.6601 | YES | 8
26 | 1.8 | 24 | 43.2 | 14 | 6.8 | 14.8114 | YES | 8
27 | 1.53 | 24 | 36.72 | 14 | 6.8 | 14.362 | YES | 8
28 | 1.79 | 24 | 42.96 | 14 | 6.8 | 14.7945 | YES | 8
29 | 2.2 | 24 | 52.8 | 14 | 6.7 | 14.9382 | YES | 8
30 | 2.16 | 24 | 51.84 | 14 | 6.5 | 13.806 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2