## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | June 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 19 | 19 | 0 | 5 | 0.01 | 0.011
2 | 19 | 19 | 0 | 5 | 0.017 | 0.017
3 | 0 | 0 | 0 | 5 | 0.093 | 0.093
4 | 0 | 0 | 0 | 5 | 0.043 | 0.043
5 | 16 | 16 | 0 | 5 | 0.019 | 0.019
6 | 0 | 0 | 0 | 5 | 0.029 | 0.029
7 | 0 | 0 | 0 | 5 | 0.013 | 0.013
8 | 0 | 0 | 0 | 5 | 0.02 | 0.02
9 | 0 | 0 | 0 | 5 | 0.028 | 0.028
10 | 0 | 0 | 0 | 5 | 0.019 | 0.019
11 | 0 | 0 | 0 | 5 | 0.025 | 0.025
12 | 0 | 0 | 0 | 5 | 0.035 | 0.035
13 | 15 | 15 | 0 | 5 | 0.011 | 0.011
14 | 15 | 15 | 0 | 5 | 0.011 | 0.011
15 | 15 | 15 | 0 | 5 | 0.014 | 0.014
16 | 15 | 15 | 0 | 5 | 0.019 | 0.019
17 | 0 | 0 | 0 | 5 | 0.015 | 0.015
18 | 0 | 0 | 0 | 5 | 0.014 | 0.014
19 | 21 | 21 | 0 | 5 | 0.014 | 0.014
20 | 22 | 22 | 0 | 5 | 0.013 | 0.013
21 | 19 | 19 | 0 | 5 | 0.09 | 0.09
22 | 19 | 19 | 0 | 5 | 0.011 | 0.011
23 | 19 | 19 | 0 | 5 | 0.022 | 0.022
24 | 0 | 0 | 0 | 5 | 0.035 | 0.035
25 | 0 | 0 | 0 | 5 | 0.011 | 0.011
26 | 0 | 0 | 0 | 5 | 0.012 | 0.012
27 | 0 | 0 | 0 | 5 | 0.024 | 0.024
28 | 18 | 18 | 0 | 5 | 0.011 | 0.011
29 | 0 | 0 | 0 | 5 | 0.0121 | 0.012
30 | 0 | 0 | 0 | 5 | 0.012 | 0.012
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE: 7/08/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
June | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | June 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 24 | 52.8 | 18 | 6.3 | 9.8337 | YES | 8
2 | 2.2 | 24 | 52.8 | 18 | 6.5 | 10.6005 | YES | 8
3 | 1.71 | 24 | 41.04 | 18 | 6.1 | 8.6159 | YES | 8
4 | 2.01 | 24 | 48.24 | 18 | 6.6 | 10.767 | YES | 8
5 | 2.09 | 24 | 50.16 | 18 | 6.6 | 10.8666 | YES | 8
6 | 1.77 | 24 | 42.48 | 18 | 6.5 | 10.0874 | YES | 8
7 | 1.5 | 24 | 36 | 18 | 6.5 | 9.7775 | YES | 8
8 | 1.26 | 24 | 30.24 | 18 | 6.7 | 10.2523 | YES | 8
9 | 1.49 | 24 | 35.76 | 18 | 6.7 | 10.5279 | YES | 8
10 | 1.71 | 24 | 41.04 | 18 | 6.7 | 10.7983 | YES | 8
11 | 1.62 | 24 | 38.88 | 18 | 6.8 | 11.0947 | YES | 8
12 | 1.59 | 24 | 38.16 | 18 | 6.9 | 11.4779 | YES | 8
13 | 1.65 | 24 | 39.6 | 18 | 6.7 | 10.7239 | YES | 8
14 | 1.31 | 24 | 31.44 | 17.5 | 6.7 | 10.6657 | YES | 8
15 | 2.2 | 24 | 52.8 | 17.1 | 6.8 | 12.5987 | YES | 8
16 | 1.99 | 24 | 47.76 | 17.3 | 7 | 13.074 | YES | 8
17 | 2.2 | 24 | 52.8 | 17.1 | 6.9 | 13.0769 | YES | 8
18 | 2.2 | 24 | 52.8 | 17.2 | 7 | 13.482 | YES | 8
19 | 2.2 | 24 | 52.8 | 17.3 | 6.9 | 12.9027 | YES | 8
20 | 2.2 | 24 | 52.8 | 16.5 | 7.2 | 15.2169 | YES | 8
21 | 1.98 | 24 | 47.52 | 16 | 7.3 | 15.9227 | YES | 8
22 | 1.99 | 24 | 47.76 | 17 | 7 | 13.3395 | YES | 8
23 | 1.93 | 24 | 46.32 | 17 | 7.1 | 13.7503 | YES | 8
24 | 1.2 | 24 | 28.8 | 18 | 6.2 | 8.4327 | YES | 8
25 | 1.33 | 24 | 31.92 | 18 | 6.3 | 8.8909 | YES | 8
26 | 1.81 | 24 | 43.44 | 18 | 6.3 | 9.3998 | YES | 8
27 | 1.5 | 24 | 36 | 17 | 6.4 | 10.0762 | YES | 8
28 | 1.87 | 24 | 44.88 | 17 | 6.4 | 10.5157 | YES | 8
29 | 1.38 | 24 | 33.12 | 18 | 7.5 | 14.0125 | YES | 8
30 | 1.42 | 24 | 34.08 | 20 | 7.7 | 13.2631 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2