## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | July 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 16 | 15 | 1 | 5 | 0.031 | 0.031
2 | 16 | 16 | 0 | 5 | 0.018 | 0.018
3 | 13 | 12 | 1 | 5 | 0.018 | 0.018
4 | 13 | 12 | 1 | 5 | 0.02 | 0.02
5 | 13 | 12 | 1 | 5 | 0.016 | 0.016
6 | 20 | 19 | 1 | 5 | 0.167 | 0.167
7 | 18 | 18 | 0 | 5 | 0.03 | 0.03
8 | 17 | 17 | 0 | 5 | 0.011 | 0.011
9 | 16 | 16 | 0 | 5 | 0.011 | 0.011
10 | 0 | 0 | 0 | 5 | 0.057 | 0.057
11 | 0 | 0 | 0 | 5 | 0.011 | 0.011
12 | 0 | 0 | 0 | 5 | 0.012 | 0.012
13 | 0 | 0 | 0 | 5 | 0.012 | 0.012
14 | 0 | 0 | 0 | 5 | 0.011 | 0.011
15 | 15 | 15 | 0 | 5 | 0.023 | 0.023
16 | 15 | 15 | 0 | 5 | 0.011 | 0.011
17 | 15 | 15 | 0 | 5 | 0.011 | 0.011
18 | 0 | 0 | 0 | 5 | 0.011 | 0.011
19 | 0 | 0 | 0 | 5 | 0.011 | 0.011
20 | 16 | 15 | 1 | 5 | 0.011 | 0.011
21 | 0 | 0 | 0 | 5 | 0.015 | 0.015
22 | 10 | 10 | 0 | 5 | 0.013 | 0.013
23 | 12 | 12 | 0 | 5 | 0.012 | 0.012
24 | 12 | 12 | 0 | 5 | 0.012 | 0.012
25 | 10 | 10 | 0 | 5 | 0.011 | 0.011
26 | 12 | 12 | 0 | 5 | 0.013 | 0.013
27 | 12 | 12 | 0 | 5 | 0.016 | 0.016
28 | 12 | 12 | 0 | 5 | 0.012 | 0.012
29 | 0 | 0 | 0 | 5 | 0.026 | 0.026
30 | 13 | 13 | 0 | 5 | 0.011 | 0.011
31 | 12 | 12 | 0 | 5 | 0.041 | 0.041
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE:8/08/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
July | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | July 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.95 | 24 | 46.8 | 20 | 6.8 | 10.0693 | YES | 8
2 | 2.05 | 24 | 49.2 | 20 | 6.9 | 10.5757 | YES | 8
3 | 2.06 | 24 | 49.44 | 18 | 6.8 | 11.6705 | YES | 8
4 | 1.71 | 24 | 41.04 | 18 | 6.9 | 11.6373 | YES | 8
5 | 1.91 | 24 | 45.84 | 20 | 6.9 | 10.4064 | YES | 8
6 | 0.82 | 24 | 19.68 | 21 | 7.9 | 12.4747 | YES | 8
7 | 2.16 | 24 | 51.84 | 22 | 7 | 9.7141 | YES | 8
8 | 2.2 | 24 | 52.8 | 22 | 6.8 | 9.051 | YES | 8
9 | 2.2 | 24 | 52.8 | 22 | 6.8 | 9.051 | YES | 8
10 | 2.2 | 24 | 52.8 | 22 | 6.8 | 9.051 | YES | 8
11 | 2.21 | 24 | 53.04 | 22 | 7 | 9.7705 | YES | 8
12 | 2.2 | 24 | 52.8 | 22 | 6.9 | 9.3987 | YES | 8
13 | 2.2 | 24 | 52.8 | 21 | 6.8 | 9.6862 | YES | 8
14 | 2 | 24 | 48 | 20 | 6.9 | 10.5149 | YES | 8
15 | 1.66 | 24 | 39.84 | 20 | 6.4 | 8.3733 | YES | 8
16 | 1.57 | 24 | 37.68 | 20 | 6.5 | 8.6056 | YES | 8
17 | 1.21 | 24 | 29.04 | 20 | 6.5 | 8.2525 | YES | 8
18 | 1.18 | 24 | 28.32 | 20 | 6.5 | 8.2237 | YES | 8
19 | 1.45 | 24 | 34.8 | 20 | 6.5 | 8.4863 | YES | 8
20 | 1.1 | 24 | 26.4 | 21 | 6.8 | 8.526 | YES | 8
21 | 1.2 | 24 | 28.8 | 21 | 6.8 | 8.6257 | YES | 8
22 | 1.4 | 24 | 33.6 | 18.9 | 6.6 | 9.4419 | YES | 8
23 | 0.7 | 24 | 16.8 | 18.8 | 6.5 | 8.4397 | YES | 8
24 | 1.3 | 24 | 31.2 | 19.3 | 6.6 | 9.0832 | YES | 8
25 | 1.5 | 24 | 36 | 19.7 | 6.6 | 9.0472 | YES | 8
26 | 1.4 | 24 | 33.6 | 18.6 | 6.6 | 9.6359 | YES | 8
27 | 1.1 | 24 | 26.4 | 19.3 | 6.5 | 8.5457 | YES | 8
28 | 1.7 | 24 | 40.8 | 19.7 | 6.6 | 9.2594 | YES | 8
29 | 1.25 | 24 | 30 | 18.1 | 6.8 | 10.5604 | YES | 8
30 | 1.05 | 24 | 25.2 | 19 | 7.1 | 10.8673 | YES | 8
31 | 1.3 | 24 | 31.2 | 18.3 | 6.9 | 10.8792 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2