## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | August 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 13 | 13 | 0 | 5 | 0.011 | 0.011
2 | 0 | 0 | 0 | 5 | 0.037 | 0.037
3 | 10 | 10 | 0 | 5 | 0.011 | 0.011
4 | 0 | 0 | 0 | 5 | 0.014 | 0.014
5 | 0 | 0 | 0 | 5 | 0.018 | 0.018
6 | 0 | 0 | 0 | 5 | 0.013 | 0.013
7 | 0 | 0 | 0 | 5 | 0.015 | 0.015
8 | 0 | 0 | 0 | 5 | 0.011 | 0.011
9 | 0 | 0 | 0 | 5 | 0.011 | 0.011
10 | 0 | 0 | 0 | 5 | 0.011 | 0.011
11 | 0 | 0 | 0 | 5 | 0.011 | 0.011
12 | 9 | 9 | 0 | 5 | 0.012 | 0.012
13 | 9 | 9 | 0 | 5 | 0.011 | 0.011
14 | 9 | 9 | 0 | 5 | 0.013 | 0.013
15 | 0 | 0 | 0 | 5 | 0.013 | 0.013
16 | 9 | 9 | 0 | 5 | 0.012 | 0.012
17 | 0 | 0 | 0 | 5 | 0.051 | 0.051
18 | 0 | 0 | 0 | 5 | 0.044 | 0.044
19 | 0 | 0 | 0 | 5 | 0.038 | 0.038
20 | 17 | 17 | 0 | 5 | 0.024 | 0.024
21 | 15 | 15 | 0 | 5 | 0.011 | 0.011
22 | 0 | 0 | 0 | 5 | 0.042 | 0.042
23 | 0 | 0 | 0 | 5 | 0.028 | 0.028
24 | 0 | 0 | 0 | 5 | 0.016 | 0.016
25 | 0 | 0 | 0 | 5 | 0.016 | 0.016
26 | 0 | 0 | 0 | 5 | 0.046 | 0.046
27 | 13 | 12 | 1 | 5 | 0.028 | 0.028
28 | 0 | 0 | 0 | 5 | 0.019 | 0.019
29 | 13 | 12 | 1 | 5 | 0.013 | 0.013
30 | 13 | 12 | 1 | 5 | 0.016 | 0.016
31 | 13 | 12 | 1 | 5 | 0.011 | 0.011
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE:9/08/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
August | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | August 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 24 | 28.8 | 18.3 | 7 | 11.1649 | YES | 8
2 | 0.9 | 24 | 21.6 | 18 | 6.8 | 10.2112 | YES | 8
3 | 1.4 | 24 | 33.6 | 18.2 | 6.6 | 9.9005 | YES | 8
4 | 1.9 | 24 | 45.6 | 19 | 6.7 | 10.3169 | YES | 8
5 | 1.22 | 24 | 29.28 | 19 | 6.6 | 9.1845 | YES | 8
6 | 1.36 | 24 | 32.64 | 19 | 7.2 | 11.691 | YES | 8
7 | 1.06 | 24 | 25.44 | 19 | 6.5 | 8.6815 | YES | 8
8 | 0.89 | 24 | 21.36 | 19 | 6.9 | 9.8973 | YES | 8
9 | 1.64 | 24 | 39.36 | 19 | 6.4 | 8.9423 | YES | 8
10 | 1.84 | 24 | 44.16 | 19 | 6.4 | 9.1522 | YES | 8
11 | 1.5 | 24 | 36 | 19 | 6.6 | 9.4873 | YES | 8
12 | 1.12 | 24 | 26.88 | 19 | 6.6 | 9.0786 | YES | 8
13 | 1.1 | 24 | 26.4 | 19 | 6.6 | 9.0576 | YES | 8
14 | 1.48 | 24 | 35.52 | 19 | 6.6 | 9.4654 | YES | 8
15 | 0.7 | 24 | 16.8 | 20 | 6.2 | 6.9358 | YES | 8
16 | 0.6 | 24 | 14.4 | 20 | 6.2 | 6.8548 | YES | 8
17 | 2.2 | 24 | 52.8 | 19 | 7 | 11.9483 | YES | 8
18 | 1.91 | 24 | 45.84 | 19 | 6.9 | 11.1327 | YES | 8
19 | 2.1 | 24 | 50.4 | 19 | 6.8 | 10.9607 | YES | 8
20 | 1.98 | 24 | 47.52 | 19 | 6.9 | 11.2227 | YES | 8
21 | 2.14 | 24 | 51.36 | 19 | 6.9 | 11.4311 | YES | 8
22 | 2.2 | 24 | 52.8 | 19 | 7 | 11.9483 | YES | 8
23 | 2.2 | 24 | 52.8 | 19 | 6.8 | 11.0876 | YES | 8
24 | 2.12 | 24 | 50.88 | 19 | 6.9 | 11.4048 | YES | 8
25 | 2.2 | 24 | 52.8 | 19 | 6.8 | 11.0876 | YES | 8
26 | 1.86 | 24 | 44.64 | 20 | 7.2 | 11.5766 | YES | 8
27 | 2.2 | 24 | 52.8 | 19 | 7.1 | 12.4025 | YES | 8
28 | 2.2 | 24 | 52.8 | 20 | 6.9 | 10.7601 | YES | 8
29 | 1.73 | 24 | 41.52 | 19 | 6.8 | 10.5033 | YES | 8
30 | 1.23 | 24 | 29.52 | 19 | 6.8 | 9.9142 | YES | 8
31 | 2.2 | 24 | 52.8 | 19 | 6.8 | 11.0876 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2