## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | September 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 15 | 14 | 1 | 5 | 0.012 | 0.012
2 | 15 | 15 | 0 | 5 | 0.015 | 0.015
3 | 12 | 12 | 0 | 5 | 0.016 | 0.016
4 | 12 | 12 | 0 | 5 | 0.018 | 0.018
5 | 12 | 12 | 0 | 5 | 0.018 | 0.018
6 | 13 | 12 | 1 | 5 | 0.011 | 0.011
7 | 12 | 12 | 0 | 5 | 0.011 | 0.011
8 | 13 | 12 | 1 | 5 | 0.011 | 0.011
9 | 12 | 12 | 0 | 5 | 0.011 | 0.011
10 | 0 | 0 | 0 | 5 | 0.041 | 0.041
11 | 0 | 0 | 0 | 5 | 0.028 | 0.028
12 | 0 | 0 | 0 | 5 | 0.012 | 0.012
13 | 16 | 16 | 0 | 5 | 0.011 | 0.011
14 | 16 | 16 | 0 | 5 | 0.012 | 0.012
15 | 0 | 0 | 0 | 5 | 0.019 | 0.019
16 | 20 | 20 | 0 | 5 | 0.011 | 0.011
17 | 0 | 0 | 0 | 5 | 0.021 | 0.021
18 | 12 | 12 | 0 | 5 | 0.011 | 0.011
19 | 12 | 11 | 1 | 5 | 0.011 | 0.011
20 | 0 | 0 | 0 | 5 | 0.011 | 0.011
21 | 13 | 13 | 0 | 5 | 0.011 | 0.011
22 | 12 | 12 | 0 | 5 | 0.018 | 0.018
23 | 0 | 0 | 0 | 5 | 0.04 | 0.04
24 | 0 | 0 | 0 | 5 | 0.016 | 0.016
25 | 0 | 0 | 0 | 5 | 0.011 | 0.011
26 | 0 | 0 | 0 | 5 | 0.022 | 0.022
27 | 14 | 14 | 0 | 5 | 0.011 | 0.011
28 | 0 | 0 | 0 | 5 | 0.018 | 0.018
29 | 0 | 0 | 0 | 5 | 0.012 | 0.012
30 | 0 | 0 | 0 | 5 | 0.012 | 0.012
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE:10/07/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
September | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | September 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 24 | 52.8 | 19 | 7.5 | 14.3926 | YES | 8
2 | 1.63 | 24 | 39.12 | 19.2 | 6.3 | 8.4844 | YES | 8
3 | 1.68 | 24 | 40.32 | 19.2 | 6.3 | 8.5339 | YES | 8
4 | 1.73 | 24 | 41.52 | 19.1 | 6.5 | 9.3199 | YES | 8
5 | 1.78 | 24 | 42.72 | 19.1 | 6.7 | 10.1064 | YES | 8
6 | 1.84 | 24 | 44.16 | 19.9 | 6.8 | 10.0097 | YES | 8
7 | 2.2 | 24 | 52.8 | 19.2 | 6.7 | 10.5368 | YES | 8
8 | 2.2 | 24 | 52.8 | 18.7 | 6.7 | 10.8984 | YES | 8
9 | 2.2 | 24 | 52.8 | 19 | 6.7 | 10.68 | YES | 8
10 | 1.92 | 24 | 46.08 | 19 | 6.7 | 10.3407 | YES | 8
11 | 1.43 | 24 | 34.32 | 19 | 6.7 | 9.7717 | YES | 8
12 | 1.84 | 24 | 44.16 | 19 | 6.7 | 10.2457 | YES | 8
13 | 1.95 | 24 | 46.8 | 19 | 6.7 | 10.3766 | YES | 8
14 | 1.71 | 24 | 41.04 | 18 | 6.7 | 10.7983 | YES | 8
15 | 1.9 | 24 | 45.6 | 18 | 6.7 | 11.0371 | YES | 8
16 | 2.2 | 24 | 52.8 | 18 | 6.8 | 11.8597 | YES | 8
17 | 1.7 | 24 | 40.8 | 18 | 6.9 | 11.624 | YES | 8
18 | 1.9 | 24 | 45.6 | 18 | 6.9 | 11.8941 | YES | 8
19 | 2.2 | 24 | 52.8 | 18 | 6.8 | 11.8597 | YES | 8
20 | 1.5 | 24 | 36 | 18 | 6.8 | 10.9425 | YES | 8
21 | 2.3 | 24 | 55.2 | 17 | 6.7 | 12.3603 | YES | 8
22 | 1.9 | 24 | 45.6 | 17 | 6.9 | 12.7203 | YES | 8
23 | 2 | 24 | 48 | 17 | 6.9 | 12.8668 | YES | 8
24 | 1.58 | 24 | 37.92 | 18 | 7.3 | 13.3092 | YES | 8
25 | 1.66 | 24 | 39.84 | 18 | 7.6 | 15.0145 | YES | 8
26 | 1.44 | 24 | 34.56 | 18 | 7.8 | 15.7693 | YES | 8
27 | 1.69 | 24 | 40.56 | 18 | 7 | 12.0524 | YES | 8
28 | 2.2 | 24 | 52.8 | 18 | 6.8 | 11.8597 | YES | 8
29 | 1.45 | 24 | 34.8 | 18 | 6.8 | 10.8797 | YES | 8
30 | 1.79 | 24 | 42.96 | 18 | 7.1 | 12.6547 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2