## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | November 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 5 | 0.025 | 0.025
2 | 0 | 0 | 0 | 5 | 0.02 | 0.02
3 | 15 | 15 | 0 | 5 | 0.022 | 0.022
4 | 15 | 15 | 0 | 5 | 0.015 | 0.015
5 | 0 | 0 | 0 | 5 | 0.016 | 0.016
6 | 0 | 0 | 0 | 5 | 0.018 | 0.018
7 | 0 | 0 | 0 | 5 | 0.013 | 0.013
8 | 10 | 10 | 0 | 5 | 0.011 | 0.011
9 | 10 | 10 | 0 | 5 | 0.013 | 0.013
10 | 0 | 0 | 0 | 5 | 0.012 | 0.012
11 | 0 | 0 | 0 | 5 | 0.014 | 0.014
12 | 0 | 0 | 0 | 5 | 0.011 | 0.011
13 | 11 | 11 | 0 | 5 | 0.012 | 0.012
14 | 0 | 0 | 0 | 5 | 0.017 | 0.017
15 | 0 | 0 | 0 | 5 | 0.018 | 0.018
16 | 15 | 14 | 1 | 5 | 0.052 | 0.052
17 | 0 | 0 | 0 | 5 | 0.019 | 0.019
18 | 0 | 0 | 0 | 5 | 0.019 | 0.019
19 | 0 | 0 | 0 | 5 | 0.012 | 0.012
20 | 0 | 0 | 0 | 5 | 0.02 | 0.02
21 | 0 | 0 | 0 | 5 | 0.023 | 0.023
22 | 15 | 15 | 0 | 5 | 0.087 | 0.087
23 | 0 | 0 | 0 | 5 | 0.018 | 0.018
24 | 10 | 10 | 0 | 5 | 0.012 | 0.012
25 | 0 | 0 | 0 | 5 | 0.022 | 0.022
26 | 10 | 10 | 0 | 5 | 0.011 | 0.011
27 | 10 | 10 | 0 | 5 | 0.011 | 0.011
28 | 0 | 0 | 0 | 5 | 0.012 | 0.012
29 | 10 | 10 | 0 | 5 | 0.011 | 0.011
30 | 10 | 10 | 0 | 5 | 0.011 | 0.011
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE:12/04/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
November | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | November 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.2 | 24 | 52.8 | 14 | 7.1 | 17.3222 | YES | 8
2 | 1.44 | 24 | 34.56 | 14 | 6.9 | 14.7527 | YES | 8
3 | 1.92 | 24 | 46.08 | 14 | 7.2 | 17.4114 | YES | 8
4 | 1.5 | 24 | 36 | 15 | 6.8 | 13.3865 | YES | 8
5 | 1.27 | 24 | 30.48 | 15 | 6.8 | 13.0387 | YES | 8
6 | 1.83 | 24 | 43.92 | 15 | 6.8 | 13.9011 | YES | 8
7 | 1.32 | 24 | 31.68 | 15 | 6.8 | 13.1136 | YES | 8
8 | 0.99 | 24 | 23.76 | 15 | 6.8 | 12.6272 | YES | 8
9 | 1.07 | 24 | 25.68 | 15 | 6.8 | 12.7435 | YES | 8
10 | 2 | 24 | 48 | 14 | 6.8 | 15.153 | YES | 8
11 | 1.85 | 24 | 44.4 | 14 | 6.8 | 14.8961 | YES | 8
12 | 2.2 | 24 | 52.8 | 13 | 6.7 | 15.9688 | YES | 8
13 | 1.76 | 24 | 42.24 | 13 | 6.7 | 15.1882 | YES | 8
14 | 1.11 | 24 | 26.64 | 13 | 6.7 | 14.1026 | YES | 8
15 | 0.71 | 24 | 17.04 | 12 | 6.7 | 14.8574 | YES | 8
16 | 1.59 | 24 | 38.16 | 12 | 6.8 | 16.9026 | YES | 8
17 | 1.99 | 24 | 47.76 | 14 | 7 | 16.2995 | YES | 8
18 | 1.4 | 24 | 33.6 | 13 | 6.6 | 14.046 | YES | 8
19 | 1.41 | 24 | 33.84 | 12 | 6.8 | 16.5737 | YES | 8
20 | 1.4 | 24 | 33.6 | 12 | 6.9 | 17.1283 | YES | 8
21 | 1.24 | 24 | 29.76 | 12 | 6.8 | 16.2698 | YES | 8
22 | 1.68 | 24 | 40.32 | 12 | 7.1 | 18.9205 | YES | 8
23 | 1.28 | 24 | 30.72 | 12 | 7 | 17.4913 | YES | 8
24 | 1.28 | 24 | 30.72 | 12 | 7 | 17.4913 | YES | 8
25 | 1.28 | 24 | 30.72 | 12 | 6.7 | 15.7981 | YES | 8
26 | 1.12 | 24 | 26.88 | 12 | 6.8 | 16.0591 | YES | 8
27 | 1.12 | 24 | 26.88 | 12 | 7 | 17.1869 | YES | 8
28 | 1.41 | 24 | 33.84 | 12 | 7 | 17.7432 | YES | 8
29 | 1.1 | 24 | 26.4 | 12 | 6.8 | 16.0243 | YES | 8
30 | 1.1 | 24 | 26.4 | 12 | 6.8 | 16.0243 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2