## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | December 2024
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 10 | 10 | 0 | 5 | 0.011 | 0.011
2 | 10 | 10 | 0 | 5 | 0.012 | 0.012
3 | 10 | 10 | 0 | 5 | 0.012 | 0.012
4 | 10 | 10 | 0 | 5 | 0.013 | 0.013
5 | 10 | 10 | 0 | 5 | 0.027 | 0.027
6 | 10 | 10 | 0 | 5 | 0.016 | 0.016
7 | 10 | 10 | 0 | 5 | 0.011 | 0.011
8 | 10 | 10 | 0 | 5 | 0.011 | 0.011
9 | 0 | 0 | 0 | 5 | 0.15 | 0.15
10 | 0 | 0 | 0 | 5 | 0.011 | 0.011
11 | 7 | 7 | 0 | 5 | 0.015 | 0.015
12 | 0 | 0 | 0 | 5 | 0.012 | 0.012
13 | 7 | 7 | 0 | 5 | 0.011 | 0.011
14 | 20 | 20 | 0 | 5 | 0.022 | 0.022
15 | 9 | 9 | 0 | 5 | 0.011 | 0.011
16 | 9 | 9 | 0 | 5 | 0.033 | 0.033
17 | 15 | 15 | 0 | 5 | 0.011 | 0.011
18 | 18 | 18 | 0 | 5 | 0.011 | 0.011
19 | 15 | 15 | 0 | 5 | 0.011 | 0.011
20 | 15 | 15 | 0 | 5 | 0.012 | 0.012
21 | 15 | 15 | 0 | 5 | 0.011 | 0.011
22 | 15 | 15 | 0 | 5 | 0.012 | 0.012
23 | 0 | 0 | 0 | 5 | 0.023 | 0.023
24 | 15 | 15 | 0 | 5 | 0.011 | 0.011
25 | 15 | 15 | 0 | 5 | 0.011 | 0.011
26 | 15 | 15 | 0 | 5 | 0.014 | 0.014
27 | 15 | 15 | 0 | 5 | 0.011 | 0.011
28 | 16 | 16 | 0 | 5 | 0.0112 | 0.012
29 | 15 | 15 | 0 | 5 | 0.012 | 0.012
30 | 15 | 15 | 0 | 5 | 0.011 | 0.011
31 | 14 | 14 | 0 | 5 | 0.014 | 0.014
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE:01/07/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
December | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | December 2024 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.08 | 24 | 25.92 | 12 | 7 | 17.1118 | YES | 8
2 | 2.2 | 24 | 52.8 | 9.6 | 6.8 | 21.1291 | YES | 8
3 | 2.2 | 24 | 52.8 | 9.6 | 6.7 | 20.4038 | YES | 8
4 | 2.2 | 24 | 52.8 | 9.6 | 6.9 | 21.8831 | YES | 8
5 | 2.2 | 24 | 52.8 | 9.6 | 6.8 | 21.1291 | YES | 8
6 | 2.03 | 24 | 48.72 | 9.6 | 7 | 22.2351 | YES | 8
7 | 2.2 | 24 | 52.8 | 9.6 | 6.8 | 21.1291 | YES | 8
8 | 2.2 | 24 | 52.8 | 9.6 | 6.8 | 21.1291 | YES | 8
9 | 2.2 | 24 | 52.8 | 9.6 | 6.9 | 21.8831 | YES | 8
10 | 2.2 | 24 | 52.8 | 9.5 | 6.8 | 21.2683 | YES | 8
11 | 2.15 | 24 | 51.6 | 9.5 | 6.9 | 21.9039 | YES | 8
12 | 2.2 | 24 | 52.8 | 9.5 | 6.8 | 21.2683 | YES | 8
13 | 1.9 | 24 | 45.6 | 9.5 | 6.9 | 21.2952 | YES | 8
14 | 1.72 | 24 | 41.28 | 9.5 | 7.1 | 22.3855 | YES | 8
15 | 2.2 | 24 | 52.8 | 10 | 7 | 22.0758 | YES | 8
16 | 2.2 | 24 | 52.8 | 11 | 6.8 | 19.2822 | YES | 8
17 | 1.2 | 24 | 28.8 | 10 | 7 | 19.7308 | YES | 8
18 | 1.15 | 24 | 27.6 | 10 | 7 | 19.6211 | YES | 8
19 | 1.51 | 24 | 36.24 | 10 | 7 | 20.4266 | YES | 8
20 | 1.75 | 24 | 42 | 12 | 7 | 18.4215 | YES | 8
21 | 1.63 | 24 | 39.12 | 12 | 7 | 18.1788 | YES | 8
22 | 2.2 | 24 | 52.8 | 12 | 7 | 19.3648 | YES | 8
23 | 2.2 | 24 | 52.8 | 12 | 6.9 | 18.7068 | YES | 8
24 | 2.2 | 24 | 52.8 | 13 | 7 | 17.8421 | YES | 8
25 | 2.2 | 24 | 52.8 | 13 | 6.8 | 16.5709 | YES | 8
26 | 2.2 | 24 | 52.8 | 12 | 6.8 | 18.074 | YES | 8
27 | 2.2 | 24 | 52.8 | 12 | 6.9 | 18.7068 | YES | 8
28 | 2.2 | 24 | 52.8 | 12 | 6.9 | 18.7068 | YES | 8
29 | 1.35 | 24 | 32.4 | 12 | 7 | 17.6264 | YES | 8
30 | 1.63 | 24 | 39.12 | 12 | 7 | 18.1788 | YES | 8
31 | 1.41 | 24 | 33.84 | 12 | 7 | 17.7432 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2