## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | January 2025
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 14 | 14 | 0 | 5 | 0.016 | 0.016
2 | 13 | 13 | 0 | 5 | 0.013 | 0.013
3 | 13 | 13 | 0 | 5 | 0.012 | 0.012
4 | 13 | 12 | 1 | 5 | 0.011 | 0.011
5 | 18 | 18 | 0 | 5 | 0.013 | 0.012
6 | 18 | 18 | 0 | 5 | 0.012 | 0.012
7 | 15 | 15 | 0 | 5 | 0.012 | 0.012
8 | 15 | 15 | 0 | 5 | 0.012 | 0.012
9 | 15 | 15 | 0 | 5 | 0.012 | 0.012
10 | 15 | 15 | 0 | 5 | 0.011 | 0.011
11 | 15 | 15 | 0 | 5 | 0.016 | 0.016
12 | 15 | 15 | 0 | 5 | 0.011 | 0.011
13 | 15 | 15 | 0 | 5 | 0.012 | 0.012
14 | 15 | 15 | 0 | 5 | 0.012 | 0.012
15 | 15 | 15 | 0 | 5 | 0.017 | 0.017
16 | 15 | 15 | 0 | 5 | 0.014 | 0.014
17 | 15 | 15 | 0 | 5 | 0.012 | 0.012
18 | 15 | 15 | 0 | 5 | 0.011 | 0.011
19 | 15 | 15 | 0 | 5 | 0.011 | 0.011
20 | 15 | 15 | 0 | 5 | 0.011 | 0.011
21 | 14 | 14 | 0 | 5 | 0.011 | 0.011
22 | 15 | 14 | 1 | 5 | 0.013 | 0.013
23 | 15 | 15 | 0 | 5 | 0.011 | 0.011
24 | 15 | 15 | 0 | 5 | 0.012 | 0.012
25 | 14 | 14 | 0 | 5 | 0.014 | 0.014
26 | 15 | 15 | 0 | 5 | 0.012 | 0.012
27 | 18 | 18 | 0 | 5 | 0.014 | 0.014
28 | 15 | 15 | 0 | 5 | 0.015 | 0.015
29 | 15 | 15 | 0 | 5 | 0.011 | 0.011
30 | 15 | 15 | 0 | 5 | 0.015 | 0.015
31 | 15 | 15 | 0 | 5 | 0.012 | 0.012
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE:02/04/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
January | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | January 2025 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.54 | 24 | 36.96 | 12 | 7 | 17.9991 | YES | 8
2 | 0.96 | 24 | 23.04 | 12 | 6.9 | 16.3251 | YES | 8
3 | 1.42 | 24 | 34.08 | 12 | 6.8 | 16.5918 | YES | 8
4 | 1.89 | 24 | 45.36 | 12 | 6.7 | 16.8819 | YES | 8
5 | 1.76 | 24 | 42.24 | 12 | 7.5 | 21.9465 | YES | 8
6 | 1.16 | 24 | 27.84 | 12 | 6.8 | 16.129 | YES | 8
7 | 1.16 | 24 | 27.84 | 12 | 6.8 | 16.129 | YES | 8
8 | 1.63 | 24 | 39.12 | 12 | 6.8 | 16.9767 | YES | 8
9 | 1.18 | 24 | 28.32 | 12 | 6.8 | 16.164 | YES | 8
10 | 1.18 | 24 | 28.32 | 12 | 6.8 | 16.164 | YES | 8
11 | 1.42 | 24 | 34.08 | 12 | 6.8 | 16.5918 | YES | 8
12 | 1.45 | 24 | 34.8 | 12 | 6.8 | 16.6462 | YES | 8
13 | 1.72 | 24 | 41.28 | 10.6 | 6.96 | 19.8304 | YES | 8
14 | 1.81 | 24 | 43.44 | 10.6 | 6.74 | 18.5617 | YES | 8
15 | 1.89 | 24 | 45.36 | 10.6 | 6.74 | 18.7269 | YES | 8
16 | 1.86 | 24 | 44.64 | 10.8 | 6.94 | 19.7442 | YES | 8
17 | 1.23 | 24 | 29.52 | 10 | 6.83 | 18.6657 | YES | 8
18 | 2.2 | 24 | 52.8 | 9.9 | 6.85 | 21.0825 | YES | 8
19 | 2.2 | 24 | 52.8 | 9.6 | 6.87 | 21.6538 | YES | 8
20 | 1.52 | 24 | 36.48 | 9.8 | 7.1 | 21.4569 | YES | 8
21 | 1.96 | 24 | 47.04 | 9.4 | 6.9 | 21.5811 | YES | 8
22 | 2.09 | 24 | 50.16 | 9.4 | 7 | 22.6846 | YES | 8
23 | 1.83 | 24 | 43.92 | 9.4 | 6.9 | 21.2674 | YES | 8
24 | 1.76 | 24 | 42.24 | 9.2 | 7.1 | 22.938 | YES | 8
25 | 1.91 | 24 | 45.84 | 9.4 | 7.1 | 23.0246 | YES | 8
26 | 2.11 | 24 | 50.64 | 9.5 | 6.9 | 21.8052 | YES | 8
27 | 1.25 | 24 | 30 | 10 | 7 | 19.8412 | YES | 8
28 | 1.75 | 24 | 42 | 10 | 7 | 20.9842 | YES | 8
29 | 1.56 | 24 | 37.44 | 10 | 7 | 20.5414 | YES | 8
30 | 1.58 | 24 | 37.92 | 10 | 7 | 20.5875 | YES | 8
31 | 1.58 | 24 | 37.92 | 10.2 | 7 | 20.3199 | YES | 8
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2