## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Coos
Cartridge or Bag Filtration | [5 empty] | Month/Year: | February 2025
System Name: | Weiss Estates Water District |  |  | ID#: 41-05581 |  | WTP ID: TP-1
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 15 | 15 | 0 | 5 | 0.016 | 0.016
2 | 16 | 16 | 0 | 5 | 0.013 | 0.013
3 | 15 | 15 | 0 | 5 | 0.015 | 0.015
4 | 14 | 14 | 0 | 5 | 0.011 | 0.011
5 | 15 | 15 | 0 | 5 | 0.011 | 0.011
6 | 14 | 14 | 0 | 5 | 0.011 | 0.011
7 | 10 | 10 | 0 | 5 | 0.013 | 0.013
8 | 9 | 9 | 0 | 5 | 0.015 | 0.015
9 | 9 | 9 | 0 | 5 | 0.025 | 0.025
10 | 9 | 9 | 0 | 5 | 0.012 | 0.012
11 | 9 | 9 | 0 | 5 | 0.014 | 0.014
12
13 | 20 | 19 | 1 | 5 | 0.017 | 0.017
14 | 12 | 12 | 0 | 5 | 0.05 | 0.05
15 | 12 | 12 | 0 | 5 | 0.012 | 0.012
16 | 12 | 12 | 0 | 5 | 0.016 | 0.016
17 | 12 | 12 | 0 | 5 | 0.011 | 0.011
18 | 12 | 12 | 0 | 5 | 0.011 | 0.011
19 | 11 | 11 | 0 | 5 | 0.011 | 0.011
20
21
22
23
24
25
26
27
28
29
30
31
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes** | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Michael Murphy
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic submit |  | DATE:03/07/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541) 253-6191 |  | CERT #: T- 09453
Note: Feb. 12, and 20-28—no production at plant. Filter off line for cleaning on Feb. 12. Feb.20-28, plant
disassembled for conversion to UV disinfection. Water purchased from City of Coos Bay, and trucked
to Weiss Estates by Bainbridge Water. Chlorine added to keep residual appropriate.
February | [6 empty] | WTP- :1
System Name: | Weiss Estates Water District |  | ID#: 41 -05581 |  | Month/Year: | February 2025 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.41 | 24 | 33.84 | 10 | 7 | 20.1992 | YES | 8
2 | 1.89 | 24 | 45.36 | 10 | 7 | 21.3172 | YES | 8
3 | 2.2 | 24 | 52.8 | 10 | 7.03 | 22.31 | YES | 8
4 | 2.2 | 24 | 52.8 | 10 | 6.94 | 21.6154 | YES | 8
5 | 1.95 | 24 | 46.8 | 9 | 7.03 | 23.1708 | YES | 8
6 | 2.2 | 24 | 52.8 | 9 | 6.96 | 23.2556 | YES | 8
7 | 2.2 | 24 | 52.8 | 9 | 7.02 | 23.7548 | YES | 8
8 | 2.17 | 24 | 52.08 | 9 | 7.05 | 23.9268 | YES | 8
9 | 2.07 | 24 | 49.68 | 9 | 7.2 | 24.95 | YES | 8
10 | 1.79 | 24 | 42.96 | 9 | 7 | 22.5146 | YES | 8
11 | 1.79 | 24 | 42.96 | 9 | 7 | 22.5146 | YES | 8
12
13 | 1.54 | 24 | 36.96 | 10 | 7.6 | 25.3263 | YES | 8
14 | 1.94 | 24 | 46.56 | 10 | 7.1 | 22.2039 | YES | 8
15 | 2.2 | 24 | 52.8 | 10 | 7.8 | 29.3612 | YES | 8
16 | 2.09 | 24 | 50.16 | 10 | 7 | 21.8032 | YES | 8
17 | 2.1 | 24 | 50.4 | 12 | 7 | 19.1506 | YES | 8
18 | 1.54 | 24 | 36.96 | 12 | 7 | 17.9991 | YES | 8
19 | 1.42 | 24 | 34.08 | 12 | 7 | 17.7627 | YES | 8
20
21
22
23
24
25
26
27
28
29
30
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2